{"text_format":"1","workbook":"xlsx","n_sheets":11,"sheets":["流出係数算出","降雨強度","流入量定義","01流出計算（Q-Tグラフ）","浸透施設能力","浸透施設能力（貯留浸透モデル_道路管理者用）","02流出計算（QT-Sグラフ）","03-①調整池容量の概算","04-①調節計算（自然調節方式）","04-②調節計算（2段）","04-③調節計算（ポンプ）"],"not_rendered":{"charts":5,"images":0,"macros":1,"external_links":0,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"流出係数算出","index":0,"n_rows":31,"n_cols":10,"rows_kept":31,"cut":false,"hidden":false,"merged":[[7,1,7,4],[26,1,30,3],[1,4,2,5],[23,2,25,3],[18,1,25,1],[8,1,17,1],[4,1,4,7],[18,2,19,3],[8,2,17,3],[6,1,6,3],[20,2,22,3]]}
[null,null,null,null,null,null,null,null,"行為前Σan","行為後Σan"]
[null,null,null,null,"流出係数算定結果",null,"行為前","行為後",{"$f":"SUM($G$9:$G$95)","v":7.4},{"$f":"SUM($H$9:$H$95)","v":7.4}]
[null,null,null,null,null,null,{"$f":"$I$4/$I$2","v":0.2},{"$f":"$J$4/$J$2","v":0.9},"行為前Σ(fn*an)","行為後Σ(fn*an)"]
[null,null,null,null,null,null,null,null,{"$f":"SUM($I$9:$I$95)","v":1.4800000000000002},{"$f":"SUM($J$9:$J$95)","v":6.66}]
[null,"雨水浸透阻害行為の技術基準として設定する流出係数"]
[]
[null,"区分",null,null,"土地利用の形態の細区分","流出係数","行為前面積\n（ha）","行為後面積\n（ha）"]
[null,"計",null,null,null,"－",{"$f":"SUM(G9:G31)","v":7.4},{"$f":"SUM(H9:H31)","v":7.4}]
[null,"宅地等に該当する土地","第１号関連",null,"宅地",0.9,null,7.4,{"$f":"$F9*$G9","v":0},{"$f":"$F9*$H9","v":6.66}]
[null,null,null,null,"池沼",1,null,null,0,0]
[null,null,null,null,"水路",1,null,null,0,0]
[null,null,null,null,"ため池",1,null,null,0,0]
[null,null,null,null,"道路(法面を有しないもの）",0.9,null,null,0,0]
[null,null,null,null,"道路（法面を有するもの）",null,null,null,0,0]
[null,null,null,null,"鉄道線路（法面を有しないもの）",0.9,null,null,0,0]
[null,null,null,null,"鉄道線路（法面を有するもの）",null,null,null,0,0]
[null,null,null,null,"飛行場（法面を有しないもの）",0.9,null,null,0,0]
[null,null,null,null,"飛行場（法面を有するもの）",null,null,null,0,0]
[null,"宅地等以外の土地","第２号\n関　連",null,"不浸透性材料により舗装された土地（法面を除く）",0.95,null,null,0,0]
[null,null,null,null,"不浸透性材料により覆われた法面",1,null,null,0,0]
[null,null,"第３号\n関　連",null,"ゴルフ場（雨水を排除するための排水施設を伴うものに限る）",0.5,null,null,0,0]
[null,null,null,null,"運動場その他これに類する施設（雨水を排除するための排水施設を伴うものに限る）",0.8,null,null,0,0]
[null,null,null,null,"ローラーその他これに類する建設機械を用いて締め固められた土地",0.5,null,null,0,0]
[null,null,"上記第１号から第３号に掲げる土地以外の土地",null,"山地",0.3,null,null,0,0]
[null,null,null,null,"人工的に造成され植生に覆われた法面",0.4,null,null,0,0]
[null,null,null,null,"林地、耕地、原野その他ローラーその他これに類する建設機械を用いて締め固められていない土地",0.2,7.4,null,{"$f":"$F26*$G26","v":1.4800000000000002},0]
[null,"そ\n\n\nの\n\n\n他",null,null,null,null,null,null,0,0]
[null,null,null,null,null,null,null,null,0,0]
[null,null,null,null,null,null,null,null,0,0]
[null,null,null,null,null,null,null,null,0,0]
[null,null,null,null,null,null,null,null,0,0]

{"sheet":"降雨強度","index":1,"n_rows":38,"n_cols":12,"rows_kept":38,"cut":false,"hidden":false,"merged":[]}
["※降雨は対象地域の降雨に変更して下さい"]
["時","分","降雨量\n（mm/h）","時","分","降雨量\n（mm/h）","時","分","降雨量\n（mm/h）","時","分","降雨量\n（mm/h）"]
[0,"0－10",2.9883685934416917,6,"0－10",4.8917219351475296,12,"0－10",59.861206357191207,18,"0－10",4.7503897836760416]
[null,"10－20",3.017941819231055,null,"10－20",4.9918152762874115,null,"10－20",37.684624639749643,null,"10－20",4.661545422273548]
[null,"20－30",3.048244746807768,null,"20－30",5.0970514262529605,null,"20－30",28.50676021421549,null,"20－30",4.5766496497490152]
[null,"30－40",3.0793063809205705,null,"30－40",5.2078611640904455,null,"30－40",23.299998621753048,null,"30－40",4.4954317288579659]
[null,"40－50",3.1111573274395141,null,"40－50",5.3247260966736576,null,"40－50",19.89290528921282,null,"40－50",4.4176456611071444]
[null,"50－60",3.1438299071514848,null,"50－60",5.4481865029699748,null,"50－60",17.468218765560891,null,"50－60",4.3430673904783816]
[1,"0－10",3.1773582795094626,7,"0－10",5.5788506925665615,13,"0－10",15.643673398409248,19,"0－10",4.2714923808565572]
[null,"10－20",3.2117785773677952,null,"10－20",5.7174062333634765,null,"10－20",14.214810427781742,null,"10－20",4.2027335098838421]
[null,"20－30",3.2471290538610447,null,"20－30",5.8646335023122447,null,"20－30",13.061696782918489,null,"20－30",4.1366192317993864]
[null,"30－40",3.2834502427397183,null,"30－40",6.0214221441890459,null,"30－40",12.10903938008255,null,"30－40",4.0729919698225103]
[null,"40－50",3.3207851336226213,null,"40－50",6.1887911991092324,null,"40－50",11.30703630954315,null,"40－50",4.0117067051221511]
[null,"50－60",3.359179363836347,null,"50－60",6.3679138969935138,null,"50－60",10.621351022252384,null,"50－60",3.9526297347509853]
[2,"0－10",3.3986814287065954,8,"0－10",6.560148442046966,14,"0－10",10.027495578107505,20,"0－10",3.8956375752777603]
[null,"10－20",3.4393429124172599,null,"10－20",6.7670765596010369,null,"10－20",9.5075078986589006,null,"10－20",3.8406159924516032]
[null,"20－30",3.4812187418590383,null,"20－30",6.9905522071278483,null,"20－30",9.0478959440322342,null,"20－30",3.78745914022943]
[null,"30－40",3.5243674661703608,null,"30－40",7.2327637450759994,null,"30－40",8.6383169764361583,null,"30－40",3.7360687949769726]
[null,"40－50",3.568851565121804,null,"40－50",7.4963141514339213,null,"40－50",8.2707014313878062,null,"40－50",3.6863536727184965]
[null,"50－60",3.6147377898516879,null,"50－60",7.7843257507125827,null,"50－60",7.9386554292810843,null,"50－60",3.6382288190704912]
[3,"0－10",3.6620975400571751,9,"0－10",8.1005787406494392,15,"0－10",7.637043364981082,21,"0－10",3.5916150629220738]
[null,"10－20",3.7110072822795246,null,"10－20",8.4496970743723523,null,"10－20",7.361690047391221,null,"10－20",3.5464385262127962]
[null,"20－30",3.7615490146476986,null,"20－30",8.8374018923281028,null,"20－30",7.1091641098267928,null,"20－30",3.5026301831198907]
[null,"30－40",3.8138107842628415,null,"30－40",9.2708632491389835,null,"30－40",6.8766178456842226,null,"30－40",3.4601254629615141]
[null,"40－50",3.8678872643516797,null,"40－50",9.7591981047303307,null,"40－50",6.6616669656472141,null,"40－50",3.4188638917644312]
[null,"50－60",3.9238803994836644,null,"50－60",10.314191516685014,null,"50－60",6.4622990838507803,null,"50－60",3.3787887681787652]
[4,"0－10",3.9819001284366777,10,"0－10",10.95136836054337,16,"0－10",6.2768031989960491,22,"0－10",3.3398468699374462]
[null,"10－20",4.0420651959550469,null,"10－20",11.691634007989705,null,"10－20",6.1037147347122982,null,"10－20",3.3019881875213741]
[null,"20－30",4.1045040664828321,null,"20－30",12.563874621966647,null,"20－30",5.9417722592754671,null,"20－30",3.2651656821219603]
[null,"30－40",4.1693559552547867,null,"30－40",13.609250793181104,null,"30－40",5.7898830757965243,null,"30－40",3.2293350653535526]
[null,"40－50",4.2367719948516651,null,"40－50",14.888645425608445,null,"40－50",5.6470956227531133,null,"40－50",3.1944545984329125]
[null,"50－60",4.3069165585852716,null,"50－60",16.496388830558715,null,"50－60",5.5125771556661221,null,"50－60",3.1604849088569154]
[5,"0－10",4.3799687660566633,11,"0－10",18.587555852753326,17,"0－10",5.3855955621870635,23,"0－10",3.1273888227983662]
[null,"10－20",4.4561242010556725,null,"10－20",21.43794089100578,null,"10－20",5.2655044402320073,null,"10－20",3.095131211673106]
[null,"20－30",4.5355968778201259,null,"20－30",25.595141490281549,null,"20－30",5.1517307728194055,null,"20－30",3.0636788514948421]
[null,"30－40",4.6186214989043037,null,"30－40",32.344866998335164,null,"30－40",5.0437646848632767,null,"30－40",3.0330002937569134]
[null,"40－50",4.7054560567280532,null,"40－50",45.751809828365793,null,"40－50",4.9411508809723728,null,"40－50",3.003065746790071]
[null,"50－60",4.796384841920144,null,"50－60",97.349876995653261,null,"50－60",4.8434814494669354,null,"50－60",2.9738469665746834]

{"sheet":"流入量定義","index":2,"n_rows":147,"n_cols":2,"rows_kept":147,"cut":false,"hidden":false,"merged":[]}
["※流出計算を実行する場合、記入する必要はありません。"]
["時刻","行為後流入量"]
["00:00:00"]
["00:10:00"]
["00:20:00"]
["00:30:00"]
["00:40:00"]
["00:50:00"]
["01:00:00"]
["01:10:00"]
["01:20:00"]
["01:30:00"]
["01:40:00"]
["01:50:00"]
["02:00:00"]
["02:10:00"]
["02:20:00"]
["02:30:00"]
["02:40:00"]
["02:50:00"]
["03:00:00"]
["03:10:00"]
["03:20:00"]
["03:30:00"]
["03:40:00"]
["03:50:00"]
["04:00:00"]
["04:10:00"]
["04:20:00"]
["04:30:00"]
["04:40:00"]
["04:50:00"]
["05:00:00"]
["05:10:00"]
["05:20:00"]
["05:30:00"]
["05:40:00"]
["05:50:00"]
["06:00:00"]
["06:10:00"]
["06:20:00"]
["06:30:00"]
["06:40:00"]
["06:50:00"]
["07:00:00"]
["07:10:00"]
["07:20:00"]
["07:30:00"]
["07:40:00"]
["07:50:00"]
["08:00:00"]
["08:10:00"]
["08:20:00"]
["08:30:00"]
["08:40:00"]
["08:50:00"]
["09:00:00"]
["09:10:00"]
["09:20:00"]
["09:30:00"]
["09:40:00"]
["09:50:00"]
["10:00:00"]
["10:10:00"]
["10:20:00"]
["10:30:00"]
["10:40:00"]
["10:50:00"]
["11:00:00"]
["11:10:00"]
["11:20:00"]
["11:30:00"]
["11:40:00"]
["11:50:00"]
["12:00:00"]
["12:10:00"]
["12:20:00"]
["12:30:00"]
["12:40:00"]
["12:50:00"]
["13:00:00"]
["13:10:00"]
["13:20:00"]
["13:30:00"]
["13:40:00"]
["13:50:00"]
["14:00:00"]
["14:10:00"]
["14:20:00"]
["14:30:00"]
["14:40:00"]
["14:50:00"]
["15:00:00"]
["15:10:00"]
["15:20:00"]
["15:30:00"]
["15:40:00"]
["15:50:00"]
["16:00:00"]
["16:10:00"]
["16:20:00"]
["16:30:00"]
["16:40:00"]
["16:50:00"]
["17:00:00"]
["17:10:00"]
["17:20:00"]
["17:30:00"]
["17:40:00"]
["17:50:00"]
["18:00:00"]
["18:10:00"]
["18:20:00"]
["18:30:00"]
["18:40:00"]
["18:50:00"]
["19:00:00"]
["19:10:00"]
["19:20:00"]
["19:30:00"]
["19:40:00"]
["19:50:00"]
["20:00:00"]
["20:10:00"]
["20:20:00"]
["20:30:00"]
["20:40:00"]
["20:50:00"]
["21:00:00"]
["21:10:00"]
["21:20:00"]
["21:30:00"]
["21:40:00"]
["21:50:00"]
["22:00:00"]
["22:10:00"]
["22:20:00"]
["22:30:00"]
["22:40:00"]
["22:50:00"]
["23:00:00"]
["23:10:00"]
["23:20:00"]
["23:30:00"]
["23:40:00"]
["23:50:00"]
["24:00"]

{"sheet":"01流出計算（Q-Tグラフ）","index":3,"n_rows":149,"n_cols":11,"rows_kept":149,"cut":false,"hidden":false,"merged":[[1,1,1,5],[1,7,1,24],[22,2,24,4],[9,2,12,4],[17,2,18,5]]}
[]
[null,"流 出 計 算 条 件",null,null,null,null,null,"流 出 計 算 結 果"]
[]
[null,null,null,null,null,null,null,"時刻","行為前流入量","行為後流入量","降雨強度"]
[null,1,"流出計算の実行",null,null,null,null,"00:00:00",0,0]
[null,null,null,null,null,null,null,"00:10:00",1.2290000000000001E-2,5.5280000000000003E-2,2.9883685934416917]
[null,null,"行為面積",{"$f":"流出係数算出!$H$8","v":7.4},"ha",null,null,"00:20:00",1.2409999999999999E-2,5.5829999999999998E-2,3.017941819231055]
[null,null,null,null,null,null,null,"00:30:00",1.2529999999999999E-2,5.6390000000000003E-2,3.048244746807768]
[null,null,"降雨量",null,null,null,null,"00:40:00",1.2659999999999999E-2,5.697E-2,3.0793063809205705]
[null,null,"※「降雨強度」シートに基準降雨を入力してください。（都道府県知事等により公示されている「基準降雨」の値に変更してください。）",null,null,null,null,"00:50:00",1.2789999999999999E-2,5.756E-2,3.1111573274395141]
[null,null,null,null,null,null,null,"01:00:00",1.2919999999999999E-2,5.8160000000000003E-2,3.1438299071514848]
[null,null,null,null,null,null,null,"01:10:00",1.306E-2,5.8779999999999999E-2,3.1773582795094626]
[null,null,null,null,null,null,null,"01:20:00",1.32E-2,5.9420000000000001E-2,3.2117785773677952]
[null,null,null,null,null,null,null,"01:30:00",1.3350000000000001E-2,6.0069999999999998E-2,3.2471290538610447]
[null,null,"流出係数",null,null,null,null,"01:40:00",1.35E-2,6.0740000000000002E-2,3.2834502427397183]
[null,null,"行為前",0.2,null,null,null,"01:50:00",1.3650000000000001E-2,6.1429999999999998E-2,3.3207851336226213]
[null,null,"行為後",0.9,null,null,null,"02:00:00",1.3809999999999999E-2,6.2140000000000001E-2,3.359179363836347]
[null,null,"※「流出係数算出」シートで算出した諸元が入力されていますが、必要に応じて申請図書記載値に上書きすることができます。",null,null,null,null,"02:10:00",1.397E-2,6.2880000000000005E-2,3.3986814287065954]
[null,null,null,null,null,null,null,"02:20:00",1.414E-2,6.3630000000000006E-2,3.4393429124172599]
[null,null,null,null,null,null,null,"02:30:00",1.431E-2,6.4399999999999999E-2,3.4812187418590383]
[null,null,"流出計算結果の指定",null,null,null,null,"02:40:00",1.4489999999999999E-2,6.5199999999999994E-2,3.5243674661703608]
[null,null,null,null,null,null,null,"02:50:00",1.4670000000000001E-2,6.6019999999999995E-2,3.568851565121804]
[null,null,"※「流入量定義」シートに計算された流出計算結果（行為後）を入力してください。",null,null,null,null,"03:00:00",1.486E-2,6.6869999999999999E-2,3.6147377898516879]
[null,null,null,null,null,null,null,"03:10:00",1.506E-2,6.7750000000000005E-2,3.6620975400571751]
[null,null,null,null,null,null,null,"03:20:00",1.5259999999999999E-2,6.8650000000000003E-2,3.7110072822795246]
[null,null,null,null,null,null,null,"03:30:00",1.546E-2,6.9589999999999999E-2,3.7615490146476986]
[null,null,"許容放流量",0.01,"m3/s",null,null,"03:40:00",1.5679999999999999E-2,7.0559999999999998E-2,3.8138107842628415]
[null,null,null,null,null,null,null,"03:50:00",1.5900000000000001E-2,7.1559999999999999E-2,3.8678872643516797]
[null,null,null,null,null,null,null,"04:00:00",1.6129999999999999E-2,7.2590000000000002E-2,3.9238803994836644]
[null,null,null,null,null,null,null,"04:10:00",1.6369999999999999E-2,7.3669999999999999E-2,3.9819001284366777]
[null,null,null,null,null,null,null,"04:20:00",1.6619999999999999E-2,7.4779999999999999E-2,4.0420651959550469]
[null,null,null,null,null,null,null,"04:30:00",1.687E-2,7.5929999999999997E-2,4.1045040664828321]
[null,null,null,null,null,null,null,"04:40:00",1.7139999999999999E-2,7.7130000000000004E-2,4.1693559552547867]
[null,null,null,null,null,null,null,"04:50:00",1.7420000000000001E-2,7.8380000000000005E-2,4.2367719948516651]
[null,null,null,null,null,null,null,"05:00:00",1.771E-2,7.9680000000000001E-2,4.3069165585852716]
[null,null,null,null,null,null,null,"05:10:00",1.8010000000000002E-2,8.1030000000000005E-2,4.3799687660566633]
[null,null,null,null,null,null,null,"05:20:00",1.8319999999999999E-2,8.2439999999999999E-2,4.4561242010556725]
[null,null,null,null,null,null,null,"05:30:00",1.865E-2,8.3909999999999998E-2,4.5355968778201259]
[null,null,null,null,null,null,null,"05:40:00",1.899E-2,8.5440000000000002E-2,4.6186214989043037]
[null,null,null,null,null,null,null,"05:50:00",1.934E-2,8.7050000000000002E-2,4.7054560567280532]
[null,null,null,null,null,null,null,"06:00:00",1.9720000000000001E-2,8.8730000000000003E-2,4.796384841920144]
[null,null,null,null,null,null,null,"06:10:00",2.0109999999999999E-2,9.0499999999999997E-2,4.8917219351475296]
[null,null,null,null,null,null,null,"06:20:00",2.052E-2,9.2350000000000002E-2,4.9918152762874115]
[null,null,null,null,null,null,null,"06:30:00",2.095E-2,9.4299999999999995E-2,5.0970514262529605]
[null,null,null,null,null,null,null,"06:40:00",2.1409999999999998E-2,9.6350000000000005E-2,5.2078611640904455]
[null,null,null,null,null,null,null,"06:50:00",2.189E-2,9.851E-2,5.3247260966736576]
[null,null,null,null,null,null,null,"07:00:00",2.24E-2,0.10079,5.4481865029699748]
[null,null,null,null,null,null,null,"07:10:00",2.2939999999999999E-2,0.10321,5.5788506925665615]
[null,null,null,null,null,null,null,"07:20:00",2.35E-2,0.10577,5.7174062333634765]
[null,null,null,null,null,null,null,"07:30:00",2.4109999999999999E-2,0.1085,5.8646335023122447]
[null,null,null,null,null,null,null,"07:40:00",2.4750000000000001E-2,0.1114,6.0214221441890459]
[null,null,null,null,null,null,null,"07:50:00",2.5440000000000001E-2,0.11448999999999999,6.1887911991092324]
[null,null,null,null,null,null,null,"08:00:00",2.6179999999999998E-2,0.11781,6.3679138969935138]
[null,null,null,null,null,null,null,"08:10:00",2.6970000000000001E-2,0.12136,6.560148442046966]
[null,null,null,null,null,null,null,"08:20:00",2.7820000000000001E-2,0.12519,6.7670765596010369]
[null,null,null,null,null,null,null,"08:30:00",2.8740000000000002E-2,0.12933,6.9905522071278483]
[null,null,null,null,null,null,null,"08:40:00",2.9729999999999999E-2,0.13381000000000001,7.2327637450759994]
[null,null,null,null,null,null,null,"08:50:00",3.082E-2,0.13868,7.4963141514339213]
[null,null,null,null,null,null,null,"09:00:00",3.2000000000000001E-2,0.14401,7.7843257507125827]
[null,null,null,null,null,null,null,"09:10:00",3.3300000000000003E-2,0.14985999999999999,8.1005787406494392]
[null,null,null,null,null,null,null,"09:20:00",3.474E-2,0.15631999999999999,8.4496970743723523]
[null,null,null,null,null,null,null,"09:30:00",3.6330000000000001E-2,0.16349,8.8374018923281028]
[null,null,null,null,null,null,null,"09:40:00",3.8109999999999998E-2,0.17151,9.2708632491389835]
[null,null,null,null,null,null,null,"09:50:00",4.0120000000000003E-2,0.18054999999999999,9.7591981047303307]
[null,null,null,null,null,null,null,"10:00:00",4.24E-2,0.19081000000000001,10.314191516685014]
[null,null,null,null,null,null,null,"10:10:00",4.5019999999999998E-2,0.2026,10.95136836054337]
[null,null,null,null,null,null,null,"10:20:00",4.8070000000000002E-2,0.21629999999999999,11.691634007989705]
[null,null,null,null,null,null,null,"10:30:00",5.1650000000000001E-2,0.23243,12.563874621966647]
[null,null,null,null,null,null,null,"10:40:00",5.595E-2,0.25176999999999999,13.609250793181104]
[null,null,null,null,null,null,null,"10:50:00",6.1210000000000001E-2,0.27544000000000002,14.888645425608445]
[null,null,null,null,null,null,null,"11:00:00",6.7820000000000005E-2,0.30518000000000001,16.496388830558715]
[null,null,null,null,null,null,null,"11:10:00",7.6420000000000002E-2,0.34387000000000001,18.587555852753326]
[null,null,null,null,null,null,null,"11:20:00",8.813E-2,0.39660000000000001,21.43794089100578]
[null,null,null,null,null,null,null,"11:30:00",0.10521999999999999,0.47350999999999999,25.595141490281549]
[null,null,null,null,null,null,null,"11:40:00",0.13297,0.59838000000000002,32.344866998335164]
[null,null,null,null,null,null,null,"11:50:00",0.18809000000000001,0.84641,45.751809828365793]
[null,null,null,null,null,null,null,"12:00:00",0.40022000000000002,1.80097,97.349876995653261]
[null,null,null,null,null,null,null,"12:10:00",0.24610000000000001,1.1074299999999999,59.861206357191207]
[null,null,null,null,null,null,null,"12:20:00",0.15493000000000001,0.69716999999999996,37.684624639749643]
[null,null,null,null,null,null,null,"12:30:00",0.11719,0.52737999999999996,28.50676021421549]
[null,null,null,null,null,null,null,"12:40:00",9.579E-2,0.43104999999999999,23.299998621753048]
[null,null,null,null,null,null,null,"12:50:00",8.1780000000000005E-2,0.36802000000000001,19.89290528921282]
[null,null,null,null,null,null,null,"13:00:00",7.1809999999999999E-2,0.32316,17.468218765560891]
[null,null,null,null,null,null,null,"13:10:00",6.4310000000000006E-2,0.28941,15.643673398409248]
[null,null,null,null,null,null,null,"13:20:00",5.8439999999999999E-2,0.26296999999999998,14.214810427781742]
[null,null,null,null,null,null,null,"13:30:00",5.3699999999999998E-2,0.24163999999999999,13.061696782918489]
[null,null,null,null,null,null,null,"13:40:00",4.9779999999999998E-2,0.22402,12.10903938008255]
[null,null,null,null,null,null,null,"13:50:00",4.648E-2,0.20918,11.30703630954315]
[null,null,null,null,null,null,null,"14:00:00",4.367E-2,0.19649,10.621351022252384]
[null,null,null,null,null,null,null,"14:10:00",4.122E-2,0.18551000000000001,10.027495578107505]
[null,null,null,null,null,null,null,"14:20:00",3.909E-2,0.17588999999999999,9.5075078986589006]
[null,null,null,null,null,null,null,"14:30:00",3.7199999999999997E-2,0.16739000000000001,9.0478959440322342]
[null,null,null,null,null,null,null,"14:40:00",3.551E-2,0.15981000000000001,8.6383169764361583]
[null,null,null,null,null,null,null,"14:50:00",3.4000000000000002E-2,0.15301000000000001,8.2707014313878062]
[null,null,null,null,null,null,null,"15:00:00",3.2640000000000002E-2,0.14687,7.9386554292810843]
[null,null,null,null,null,null,null,"15:10:00",3.1399999999999997E-2,0.14129,7.637043364981082]
[null,null,null,null,null,null,null,"15:20:00",3.0259999999999999E-2,0.13619000000000001,7.361690047391221]
[null,null,null,null,null,null,null,"15:30:00",2.9229999999999999E-2,0.13152,7.1091641098267928]
[null,null,null,null,null,null,null,"15:40:00",2.827E-2,0.12722,6.8766178456842226]
[null,null,null,null,null,null,null,"15:50:00",2.7390000000000001E-2,0.12324,6.6616669656472141]
[null,null,null,null,null,null,null,"16:00:00",2.657E-2,0.11955,6.4622990838507803]
[null,null,null,null,null,null,null,"16:10:00",2.58E-2,0.11612,6.2768031989960491]
[null,null,null,null,null,null,null,"16:20:00",2.5090000000000001E-2,0.11292000000000001,6.1037147347122982]
[null,null,null,null,null,null,null,"16:30:00",2.443E-2,0.10992,5.9417722592754671]
[null,null,null,null,null,null,null,"16:40:00",2.3800000000000002E-2,0.10711,5.7898830757965243]
[null,null,null,null,null,null,null,"16:50:00",2.3220000000000001E-2,0.10446999999999999,5.6470956227531133]
[null,null,null,null,null,null,null,"17:00:00",2.266E-2,0.10198,5.5125771556661221]
[null,null,null,null,null,null,null,"17:10:00",2.214E-2,9.9629999999999996E-2,5.3855955621870635]
[null,null,null,null,null,null,null,"17:20:00",2.1649999999999999E-2,9.7409999999999997E-2,5.2655044402320073]
[null,null,null,null,null,null,null,"17:30:00",2.1180000000000001E-2,9.5310000000000006E-2,5.1517307728194055]
[null,null,null,null,null,null,null,"17:40:00",2.0740000000000001E-2,9.3310000000000004E-2,5.0437646848632767]
[null,null,null,null,null,null,null,"17:50:00",2.0310000000000002E-2,9.1410000000000005E-2,4.9411508809723728]
[null,null,null,null,null,null,null,"18:00:00",1.9910000000000001E-2,8.9599999999999999E-2,4.8434814494669354]
[null,null,null,null,null,null,null,"18:10:00",1.9529999999999999E-2,8.788E-2,4.7503897836760416]
[null,null,null,null,null,null,null,"18:20:00",1.916E-2,8.6239999999999997E-2,4.661545422273548]
[null,null,null,null,null,null,null,"18:30:00",1.882E-2,8.4669999999999995E-2,4.5766496497490152]
[null,null,null,null,null,null,null,"18:40:00",1.848E-2,8.3169999999999994E-2,4.4954317288579659]
[null,null,null,null,null,null,null,"18:50:00",1.8159999999999999E-2,8.1729999999999997E-2,4.4176456611071444]
[null,null,null,null,null,null,null,"19:00:00",1.7850000000000001E-2,8.0350000000000005E-2,4.3430673904783816]
[null,null,null,null,null,null,null,"19:10:00",1.7559999999999999E-2,7.9020000000000007E-2,4.2714923808565572]
[null,null,null,null,null,null,null,"19:20:00",1.728E-2,7.775E-2,4.2027335098838421]
[null,null,null,null,null,null,null,"19:30:00",1.7010000000000001E-2,7.6530000000000001E-2,4.1366192317993864]
[null,null,null,null,null,null,null,"19:40:00",1.6740000000000001E-2,7.535E-2,4.0729919698225103]
[null,null,null,null,null,null,null,"19:50:00",1.6490000000000001E-2,7.4219999999999994E-2,4.0117067051221511]
[null,null,null,null,null,null,null,"20:00:00",1.6250000000000001E-2,7.3120000000000004E-2,3.9526297347509853]
[null,null,null,null,null,null,null,"20:10:00",1.602E-2,7.2069999999999995E-2,3.8956375752777603]
[null,null,null,null,null,null,null,"20:20:00",1.5789999999999998E-2,7.1050000000000002E-2,3.8406159924516032]
[null,null,null,null,null,null,null,"20:30:00",1.5570000000000001E-2,7.0069999999999993E-2,3.78745914022943]
[null,null,null,null,null,null,null,"20:40:00",1.536E-2,6.9120000000000001E-2,3.7360687949769726]
[null,null,null,null,null,null,null,"20:50:00",1.516E-2,6.8199999999999997E-2,3.6863536727184965]
[null,null,null,null,null,null,null,"21:00:00",1.4959999999999999E-2,6.7309999999999995E-2,3.6382288190704912]
[null,null,null,null,null,null,null,"21:10:00",1.477E-2,6.6439999999999999E-2,3.5916150629220738]
[null,null,null,null,null,null,null,"21:20:00",1.4579999999999999E-2,6.5610000000000002E-2,3.5464385262127962]
[null,null,null,null,null,null,null,"21:30:00",1.44E-2,6.4799999999999996E-2,3.5026301831198907]
[null,null,null,null,null,null,null,"21:40:00",1.422E-2,6.4009999999999997E-2,3.4601254629615141]
[null,null,null,null,null,null,null,"21:50:00",1.406E-2,6.3250000000000001E-2,3.4188638917644312]
[null,null,null,null,null,null,null,"22:00:00",1.389E-2,6.2509999999999996E-2,3.3787887681787652]
[null,null,null,null,null,null,null,"22:10:00",1.3729999999999999E-2,6.1789999999999998E-2,3.3398468699374462]
[null,null,null,null,null,null,null,"22:20:00",1.357E-2,6.1089999999999998E-2,3.3019881875213741]
[null,null,null,null,null,null,null,"22:30:00",1.342E-2,6.0409999999999998E-2,3.2651656821219603]
[null,null,null,null,null,null,null,"22:40:00",1.328E-2,5.9740000000000001E-2,3.2293350653535526]
[null,null,null,null,null,null,null,"22:50:00",1.3129999999999999E-2,5.91E-2,3.1944545984329125]
[null,null,null,null,null,null,null,"23:00:00",1.299E-2,5.8470000000000001E-2,3.1604849088569154]
[null,null,null,null,null,null,null,"23:10:00",1.286E-2,5.7860000000000002E-2,3.1273888227983662]
[null,null,null,null,null,null,null,"23:20:00",1.272E-2,5.7259999999999998E-2,3.095131211673106]
[null,null,null,null,null,null,null,"23:30:00",1.26E-2,5.6680000000000001E-2,3.0636788514948421]
[null,null,null,null,null,null,null,"23:40:00",1.247E-2,5.611E-2,3.0330002937569134]
[null,null,null,null,null,null,null,"23:50:00",1.235E-2,5.5559999999999998E-2,3.003065746790071]
[null,null,null,null,null,null,null,1,1.223E-2,5.5019999999999999E-2,2.9738469665746834]

{"sheet":"浸透施設能力","index":4,"n_rows":62,"n_cols":19,"rows_kept":62,"cut":false,"hidden":false,"merged":[[1,1,1,6],[1,12,1,17],[2,2,2,3],[2,6,2,7],[2,13,2,14],[2,17,2,18],[3,2,3,3],[3,13,3,14],[7,1,9,1],[7,2,7,3],[7,4,9,4],[7,5,7,7],[7,12,9,12],[7,13,9,13],[7,14,9,14],[8,2,9,2],[8,3,9,3],[21,1,23,1],[21,2,21,3],[21,4,23,4],[21,5,21,7],[35,1,37,1],[35,2,35,3],[35,4,37,4],[35,5,35,7],[22,2,23,2],[36,2,37,2],[49,13,51,13],[49,14,51,14],[21,13,23,13],[21,14,23,14],[22,3,23,3],[21,12,23,12],[35,14,37,14],[35,13,37,13],[35,12,37,12],[36,3,37,3],[49,1,51,1],[49,2,49,3],[49,4,51,4],[49,5,49,7],[49,12,51,12],[50,2,51,2],[50,3,51,3]]}
[]
[null,"浸透施設能力算定結果",null,null,null,null,null,null,null,null,null,null,"空隙貯留量算定結果"]
[null,"浸透マス","浸透トレンチ",null,"透水性舗装","その他","浸透施設能力算定結果",null,null,null,null,null,"浸透マス","浸透トレンチ",null,"透水性舗装","その他","空隙貯留量算定結果"]
[null,{"$f":"SUM(I11:J20)","v":0},{"$f":"SUM(J25:J34)","v":0},null,{"$f":"SUM(J39:J48)","v":46.691999999999993},{"$f":"SUM(J53:J62)","v":0},{"$f":"B4+C4+E4+F4","v":46.691999999999993},"ｍ3/ｈｒ",null,null,null,null,{"$f":"SUM(K11:K20)/100","v":0},{"$f":"SUM(K25:K34)/100","v":0},null,{"$f":"SUM(K39:K48)/100","v":0},{"$f":"SUM(K53:K62)/100","v":0},{"$f":"M4+N4+P4+Q4","v":0},"ｍ3"]
[null,null,null,null,null,null,{"$f":"G4/3600","v":1.2969999999999999E-2},"ｍ3/s"]
[]
[null,"条件設定",null,null,null,null,null,null,null,null,null,null,"条件設定"]
[null,"【浸透マス】","単位設計浸透能（ｍ3/ｈｒ/個）",null,"設置数量\n（個）","影響係数",null,null,null,null,null,null,"【浸透マス】","体積\n（ｍ3）","空隙率\n（％）"]
[null,null,"比浸透量（㎡）","飽和透水係数\n（m/hr）",null,"（1）","（2）","（3）"]
[null,null,null,null,null,"内容（１）","内容（２）","内容（３）"]
[null,1,null,null,null,1,1,1,null,{"$f":"$C11*$D11*$E11*$F11*$G11*$H11","v":0},{"$f":"$N11*O11","v":0},null,1]
[null,2,null,null,null,1,1,1,null,{"$f":"$C12*$D12*$E12*$F12*$G12*$H12","v":0},{"$f":"$N12*O12","v":0},null,2]
[null,3,null,null,null,1,1,1,null,0,0,null,3]
[null,4,null,null,null,1,1,1,null,0,0,null,4]
[null,5,null,null,null,1,1,1,null,0,0,null,5]
[null,6,null,null,null,1,1,1,null,0,0,null,6]
[null,7,null,null,null,1,1,1,null,0,0,null,7]
[null,8,null,null,null,1,1,1,null,0,0,null,8]
[null,9,null,null,null,1,1,1,null,0,0,null,9]
[null,10,null,null,null,1,1,1,null,0,0,null,10]
[]
[null,"【浸透トレンチ】","単位設計浸透能（ｍ3/ｈｒ/m）",null,"設置数量\n（ｍ）","影響係数",null,null,null,null,null,null,"【浸透トレンチ】","体積\n（ｍ3）","空隙率\n（％）"]
[null,null,"比浸透量（㎡）","飽和透水係数\n（m/hr）",null,"（1）","（2）","（3）"]
[null,null,null,null,null,"内容（１）","内容（２）","内容（３）"]
[null,1,null,null,null,1,1,1,null,{"$f":"$C25*$D25*$E25*$F25*$G25*$H25","v":0},{"$f":"$N25*O25","v":0},null,1]
[null,2,null,null,null,1,1,1,null,{"$f":"$C26*$D26*$E26*$F26*$G26*$H26","v":0},0,null,2]
[null,3,null,null,null,1,1,1,null,0,0,null,3]
[null,4,null,null,null,1,1,1,null,0,0,null,4]
[null,5,null,null,null,1,1,1,null,0,0,null,5]
[null,6,null,null,null,1,1,1,null,0,0,null,6]
[null,7,null,null,null,1,1,1,null,0,0,null,7]
[null,8,null,null,null,1,1,1,null,0,0,null,8]
[null,9,null,null,null,1,1,1,null,0,0,null,9]
[null,10,null,null,null,1,1,1,null,0,0,null,10]
[]
[null,"【透水性舗装】","単位設計浸透能（ｍ3/ｈｒ/㎡）",null,"設置数量\n（㎡）","影響係数",null,null,null,null,null,null,"【透水性塗装】","体積\n（ｍ3）","空隙率\n（％）"]
[null,null,"比浸透量（㎡）","飽和透水係数\n（m/hr）",null,"（1）","（2）","（3）"]
[null,null,null,null,null,"内容（１）","内容（２）","内容（３）"]
[null,1,1.2969999999999999,7.1999999999999998E-3,5000,1,1,1,null,{"$f":"$C39*$D39*$E39*$F39*$G39*$H39","v":46.691999999999993},{"$f":"$N39*O39","v":0},null,1,null,10]
[null,2,null,null,null,1,1,1,null,{"$f":"$C40*$D40*$E40*$F40*$G40*$H40","v":0},{"$f":"$N40*O40","v":0},null,2]
[null,3,null,null,null,1,1,1,null,0,0,null,3]
[null,4,null,null,null,1,1,1,null,0,0,null,4]
[null,5,null,null,null,1,1,1,null,0,0,null,5]
[null,6,null,null,null,1,1,1,null,0,0,null,6]
[null,7,null,null,null,1,1,1,null,0,0,null,7]
[null,8,null,null,null,1,1,1,null,0,0,null,8]
[null,9,null,null,null,1,1,1,null,0,0,null,9]
[null,10,null,null,null,1,1,1,null,0,0,null,10]
[]
[null,"【その他】","単位設計浸透能（ｍ3/ｈｒ/単位）",null,"設置数量\n（単位）","影響係数",null,null,null,null,null,null,"【その他】","体積\n（ｍ3）","空隙率\n（％）"]
[null,null,"比浸透量（㎡）","飽和透水係数\n（m/hr）",null,"（1）","（2）","（3）"]
[null,null,null,null,null,"内容（１）","内容（２）","内容（３）"]
[null,1,null,null,null,1,1,1,null,{"$f":"$C53*$D53*$E53*$F53*$G53*$H53","v":0},{"$f":"$N53*O53","v":0},null,1]
[null,2,null,null,null,1,1,1,null,0,0,null,2]
[null,3,null,null,null,1,1,1,null,0,0,null,3]
[null,4,null,null,null,1,1,1,null,0,0,null,4]
[null,5,null,null,null,1,1,1,null,0,0,null,5]
[null,6,null,null,null,1,1,1,null,0,0,null,6]
[null,7,null,null,null,1,1,1,null,0,0,null,7]
[null,8,null,null,null,1,1,1,null,0,0,null,8]
[null,9,null,null,null,1,1,1,null,0,0,null,9]
[null,10,null,null,null,1,1,1,null,0,0,null,10]

{"sheet":"浸透施設能力（貯留浸透モデル_道路管理者用）","index":5,"n_rows":58,"n_cols":19,"rows_kept":58,"cut":false,"hidden":false,"merged":[[6,1,7,1],[6,6,6,7],[7,6,7,7],[1,7,1,8],[2,1,2,6],[4,1,4,2],[5,1,5,2],[5,6,5,7],[15,1,15,2],[15,9,15,10],[8,1,9,1],[8,6,8,7],[9,6,9,7],[10,1,10,6],[11,1,11,3],[12,1,12,2],[12,9,12,10],[13,1,13,2],[13,9,13,10],[14,1,14,2],[14,9,14,10],[16,1,16,2],[16,9,16,10],[17,1,17,2],[17,9,17,10],[18,1,18,2],[18,9,18,10],[27,1,27,2],[28,1,28,2],[21,1,21,6],[23,1,25,2],[23,3,23,4],[23,5,25,5],[23,6,25,6],[26,1,26,2],[23,18,25,18],[24,3,25,3],[24,4,25,4],[24,7,25,7],[24,8,25,8],[23,16,25,16],[23,17,25,17],[23,10,25,10],[23,11,25,11],[23,12,25,12],[23,15,25,15],[23,7,23,8],[29,1,29,2],[30,1,30,2],[31,1,31,2],[38,3,39,3],[38,4,39,4],[32,1,32,2],[33,1,33,2],[34,1,34,2],[35,1,35,2],[37,1,39,2],[37,3,37,4],[37,10,39,10],[37,11,39,11],[37,12,39,12],[52,6,52,7],[40,1,40,2],[41,1,41,2],[42,1,42,2],[43,1,43,2],[44,1,44,2],[45,1,45,2],[38,7,39,7],[38,8,39,8],[37,5,39,5],[37,6,39,6],[37,7,37,8],[53,1,53,2],[54,1,54,2],[46,1,46,2],[47,1,47,2],[48,1,48,2],[49,1,49,2],[52,1,52,2]]}
[]
["透水性舗装",null,null,null,null,null,null,"部分を入力して下さい"]
[]
[null,"基本諸元"]
[null,"設置数量(舗装面積) (m2)",null,3000]
[null,"飽和透水係数 （m/hr）",null,7.1999999999999998E-3,null,null,"上層路盤での貯留率(%)",null,{"$f":"L17","v":12.5}]
[null,"比浸透量算定定数\nK=aH+b","a",1.4E-2,null,null,"下層路盤での貯留率(%)",null,{"$f":"L18","v":4.5}]
[null,null,"b",1.2869999999999999,null,null,"下層路盤厚(mm)",null,{"$f":"D18","v":400}]
[null,"目詰まり\n係数","C1",0.9,null,null,"下層路盤での貯留量(mm)",null,{"$f":"M18","v":18}]
[null,null,"C2",0.9,null,null,"貯留量の合計(mm)",null,{"$f":"M19","v":55.5}]
[]
[null,"貯留率と水拘束率"]
[null,null,null,"厚さ(mm)","空気間隙率\n(%)","空気間隙率との関係","水拘束率\n(%)","水拘束量\n(mm)","貯留率\n(%)","貯留量\n(mm)",null,"STEP2での\n貯留率\n(%)","STEP2での\n貯留量\n(mm)"]
[null,"関係式",null,"a","b","b'","c","a×c/100","d (=b+b')","a×d/100",null,"d-c","a×(d-c)/100"]
[null,"表層",null,50,20,-6,1.5,{"$f":"D15*G15/100","v":0.75},{"$f":"E15+F15","v":14},{"$f":"D15*I15/100","v":7},null,{"$f":"I15-G15","v":12.5},{"$f":"D15*(I15-G15)/100","v":6.25}]
[null,"中間層・基層",null,100,20,-6,1.5,{"$f":"D16*G16/100","v":1.5},{"$f":"E16+F16","v":14},{"$f":"D16*I16/100","v":14},null,{"$f":"I16-G16","v":12.5},{"$f":"D16*(I16-G16)/100","v":12.5}]
[null,"上層路盤",null,150,20,-6,1.5,{"$f":"D17*G17/100","v":2.25},{"$f":"E17+F17","v":14},{"$f":"D17*I17/100","v":21},null,{"$f":"I17-G17","v":12.5},{"$f":"D17*(I17-G17)/100","v":18.75}]
[null,"下層路盤",null,400,8,-3,0.5,{"$f":"D18*G18/100","v":2},{"$f":"E18+F18","v":5},{"$f":"D18*I18/100","v":20},null,{"$f":"I18-G18","v":4.5},{"$f":"D18*(I18-G18)/100","v":18}]
[null,"合計",null,{"$f":"SUM(D15:D18)","v":700},"-","-","-",{"$f":"SUM(H15:H18)","v":6.5},"-",{"$f":"SUM(J15:J18)","v":62},null,"-",{"$f":"SUM(M15:M18)","v":55.5}]
[]
["浸透マス・トレンチ"]
[]
[null,"浸透能諸元",null,null,null,null,null,null,null,null,"空隙貯留諸元"]
[null,"【浸透マス】",null,"単位設計浸透能（ｍ3/ｈｒ/個）",null,"設置数量\n（個）","設計水頭\n(m)","影響係数",null,null,"【浸透\nマス】","体積\n（ｍ3）","空隙率\n（％）",null,null,"Σ","設計浸透量","平均設計水頭","設計空隙貯留量"]
[null,null,null,"比浸透量（㎡）","飽和透水係数\n（m/hr）",null,null,"地下水位\n係数","目詰まり\n係数"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"小計"]
[null,1,null,10,7.1999999999999998E-3,10,0.8,1,1,null,1,500,20,null,null,{"$f":"D27*E27*F27*G27*H27*I27","v":0.57599999999999996},{"$f":"D27*E27*F27*H27*I27","v":0.72},null,{"$f":"L27*M27/100","v":100}]
[null,2,null,null,null,null,null,1,1,null,2,null,null,null,null,{"$f":"D28*E28*F28*G28*H28*I28","v":0},{"$f":"D28*E28*F28*H28*I28","v":0},null,{"$f":"L28*M28/100","v":0}]
[null,3,null,null,null,null,null,1,1,null,3,null,null,null,null,0,0,null,0]
[null,4,null,null,null,null,null,1,1,null,4,null,null,null,null,0,0,null,0]
[null,5,null,null,null,null,null,1,1,null,5,null,null,null,null,0,0,null,0]
[null,6,null,null,null,null,null,1,1,null,6,null,null,null,null,0,0,null,0]
[null,7,null,null,null,null,null,1,1,null,7,null,null,null,null,0,0,null,0]
[null,8,null,null,null,null,null,1,1,null,8,null,null,null,null,0,0,null,0]
[null,9,null,null,null,null,null,1,1,null,9,null,null,null,null,0,0,null,0]
[null,10,null,null,null,null,null,1,1,null,10,null,null,null,null,0,0,null,0]
[]
[null,"【浸透トレンチ】",null,"単位設計浸透能（ｍ3/ｈｒ/m）",null,"設置数量\n（ｍ）","設計水頭\n(m)","影響係数",null,null,"【浸透\nトレンチ】","体積\n（ｍ3）","空隙率\n（％）"]
[null,null,null,"比浸透量（㎡）","飽和透水係数\n（m/hr）",null,null,"地下水位\n係数","目詰まり\n係数"]
[]
[null,1,null,null,null,null,null,1,1,null,1,null,null,null,null,{"$f":"D41*E41*F41*G41*H41*I41","v":0},{"$f":"D41*E41*F41*H41*I41","v":0},null,{"$f":"L41*M41/100","v":0}]
[null,2,null,null,null,null,null,1,1,null,2,null,null,null,null,{"$f":"D42*E42*F42*G42*H42*I42","v":0},{"$f":"D42*E42*F42*H42*I42","v":0},null,0]
[null,3,null,null,null,null,null,1,1,null,3,null,null,null,null,0,0,null,0]
[null,4,null,null,null,null,null,1,1,null,4,null,null,null,null,0,0,null,0]
[null,5,null,null,null,null,null,1,1,null,5,null,null,null,null,0,0,null,0]
[null,6,null,null,null,null,null,1,1,null,6,null,null,null,null,0,0,null,0]
[null,7,null,null,null,null,null,1,1,null,7,null,null,null,null,0,0,null,0]
[null,8,null,null,null,null,null,1,1,null,8,null,null,null,null,0,0,null,0]
[null,9,null,null,null,null,null,1,1,null,9,null,null,null,null,0,0,null,0]
[null,10,null,null,null,null,null,1,1,null,10,null,null,null,null,0,0,null,0]
[]
[null,"統合諸元"]
[null,"設計浸透能(m3/hr)",null,{"$f":"Q55","v":0.72}]
[null,"平均設計水頭(m)",null,{"$f":"IF(D53>0,+R55,0)","v":0.79999999999999993}]
[null,"設計空隙貯留量(m3)",null,{"$f":"S55","v":100},null,null,null,null,null,null,null,null,null,null,"総合計",{"$f":"P57+P58","v":0.57599999999999996},{"$f":"Q57+Q58","v":0.72},{"$f":"P55/Q55","v":0.79999999999999993},{"$f":"S57+S58","v":100}]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"マス",{"$f":"SUM(P27:P36)","v":0.57599999999999996},{"$f":"SUM(Q27:Q36)","v":0.72},{"$f":"P57/Q57","v":0.79999999999999993},{"$f":"SUM(S27:S36)","v":100}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"トレンチ",{"$f":"SUM(P41:P50)","v":0},{"$f":"SUM(Q41:Q50)","v":0},{"$f":"P58/Q58","v":{"$error":"#DIV/0!"}},{"$f":"SUM(S41:S50)","v":0}]

{"sheet":"02流出計算（QT-Sグラフ）","index":6,"n_rows":149,"n_cols":10,"rows_kept":149,"cut":false,"hidden":false,"merged":[[7,2,8,5],[12,2,14,5],[1,1,1,5],[1,7,1,23]]}
[]
[null,"流 出 計 算 条 件",null,null,null,null,null,"流 出 計 算 結 果"]
[]
[null,null,null,null,null,null,null,"時刻","浸透考慮前","浸透考慮後"]
[null,1,"浸透施設なし",null,null,null,null,"00:00:00",0,0]
[null,null,null,null,null,null,null,"00:10:00",5.5280000000000003E-2,5.5280000000000003E-2]
[null,null,"浸透施設あり",null,null,null,null,"00:20:00",5.5829999999999998E-2,5.5829999999999998E-2]
[null,null,"※「浸透施設能力」シートに浸透施設諸元を入力してください。",null,null,null,null,"00:30:00",5.6390000000000003E-2,5.6390000000000003E-2]
[null,null,null,null,null,null,null,"00:40:00",5.697E-2,5.697E-2]
[null,null,null,null,null,null,null,"00:50:00",5.756E-2,5.756E-2]
[null,null,"浸透施設あり",null,null,null,null,"01:00:00",5.8160000000000003E-2,5.8160000000000003E-2]
[null,null,"（貯留浸透モデル_道路管理者用）",null,null,null,null,"01:10:00",5.8779999999999999E-2,5.8779999999999999E-2]
[null,null,"※「浸透施設能力（貯留浸透モデル_道路管理者用）」シートに浸透施設諸元を入力してください。",null,null,null,null,"01:20:00",5.9420000000000001E-2,5.9420000000000001E-2]
[null,null,null,null,null,null,null,"01:30:00",6.0069999999999998E-2,6.0069999999999998E-2]
[null,null,null,null,null,null,null,"01:40:00",6.0740000000000002E-2,6.0740000000000002E-2]
[null,null,null,null,null,null,null,"01:50:00",6.1429999999999998E-2,6.1429999999999998E-2]
[null,null,null,null,null,null,null,"02:00:00",6.2140000000000001E-2,6.2140000000000001E-2]
[null,null,null,null,null,null,null,"02:10:00",6.2880000000000005E-2,6.2880000000000005E-2]
[null,null,null,null,null,null,null,"02:20:00",6.3630000000000006E-2,6.3630000000000006E-2]
[null,null,null,null,null,null,null,"02:30:00",6.4399999999999999E-2,6.4399999999999999E-2]
[null,null,null,null,null,null,null,"02:40:00",6.5199999999999994E-2,6.5199999999999994E-2]
[null,null,null,null,null,null,null,"02:50:00",6.6019999999999995E-2,6.6019999999999995E-2]
[null,null,null,null,null,null,null,"03:00:00",6.6869999999999999E-2,6.6869999999999999E-2]
[null,null,null,null,null,null,null,"03:10:00",6.7750000000000005E-2,6.7750000000000005E-2]
[null,null,null,null,null,null,null,"03:20:00",6.8650000000000003E-2,6.8650000000000003E-2]
[null,null,null,null,null,null,null,"03:30:00",6.9589999999999999E-2,6.9589999999999999E-2]
[null,null,null,null,null,null,null,"03:40:00",7.0559999999999998E-2,7.0559999999999998E-2]
[null,null,null,null,null,null,null,"03:50:00",7.1559999999999999E-2,7.1559999999999999E-2]
[null,null,null,null,null,null,null,"04:00:00",7.2590000000000002E-2,7.2590000000000002E-2]
[null,null,null,null,null,null,null,"04:10:00",7.3669999999999999E-2,7.3669999999999999E-2]
[null,null,null,null,null,null,null,"04:20:00",7.4779999999999999E-2,7.4779999999999999E-2]
[null,null,null,null,null,null,null,"04:30:00",7.5929999999999997E-2,7.5929999999999997E-2]
[null,null,null,null,null,null,null,"04:40:00",7.7130000000000004E-2,7.7130000000000004E-2]
[null,null,null,null,null,null,null,"04:50:00",7.8380000000000005E-2,7.8380000000000005E-2]
[null,null,null,null,null,null,null,"05:00:00",7.9680000000000001E-2,7.9680000000000001E-2]
[null,null,null,null,null,null,null,"05:10:00",8.1030000000000005E-2,8.1030000000000005E-2]
[null,null,null,null,null,null,null,"05:20:00",8.2439999999999999E-2,8.2439999999999999E-2]
[null,null,null,null,null,null,null,"05:30:00",8.3909999999999998E-2,8.3909999999999998E-2]
[null,null,null,null,null,null,null,"05:40:00",8.5440000000000002E-2,8.5440000000000002E-2]
[null,null,null,null,null,null,null,"05:50:00",8.7050000000000002E-2,8.7050000000000002E-2]
[null,null,null,null,null,null,null,"06:00:00",8.8730000000000003E-2,8.8730000000000003E-2]
[null,null,null,null,null,null,null,"06:10:00",9.0499999999999997E-2,9.0499999999999997E-2]
[null,null,null,null,null,null,null,"06:20:00",9.2350000000000002E-2,9.2350000000000002E-2]
[null,null,null,null,null,null,null,"06:30:00",9.4299999999999995E-2,9.4299999999999995E-2]
[null,null,null,null,null,null,null,"06:40:00",9.6350000000000005E-2,9.6350000000000005E-2]
[null,null,null,null,null,null,null,"06:50:00",9.851E-2,9.851E-2]
[null,null,null,null,null,null,null,"07:00:00",0.10079,0.10079]
[null,null,null,null,null,null,null,"07:10:00",0.10321,0.10321]
[null,null,null,null,null,null,null,"07:20:00",0.10577,0.10577]
[null,null,null,null,null,null,null,"07:30:00",0.1085,0.1085]
[null,null,null,null,null,null,null,"07:40:00",0.1114,0.1114]
[null,null,null,null,null,null,null,"07:50:00",0.11448999999999999,0.11448999999999999]
[null,null,null,null,null,null,null,"08:00:00",0.11781,0.11781]
[null,null,null,null,null,null,null,"08:10:00",0.12136,0.12136]
[null,null,null,null,null,null,null,"08:20:00",0.12519,0.12519]
[null,null,null,null,null,null,null,"08:30:00",0.12933,0.12933]
[null,null,null,null,null,null,null,"08:40:00",0.13381000000000001,0.13381000000000001]
[null,null,null,null,null,null,null,"08:50:00",0.13868,0.13868]
[null,null,null,null,null,null,null,"09:00:00",0.14401,0.14401]
[null,null,null,null,null,null,null,"09:10:00",0.14985999999999999,0.14985999999999999]
[null,null,null,null,null,null,null,"09:20:00",0.15631999999999999,0.15631999999999999]
[null,null,null,null,null,null,null,"09:30:00",0.16349,0.16349]
[null,null,null,null,null,null,null,"09:40:00",0.17151,0.17151]
[null,null,null,null,null,null,null,"09:50:00",0.18054999999999999,0.18054999999999999]
[null,null,null,null,null,null,null,"10:00:00",0.19081000000000001,0.19081000000000001]
[null,null,null,null,null,null,null,"10:10:00",0.2026,0.2026]
[null,null,null,null,null,null,null,"10:20:00",0.21629999999999999,0.21629999999999999]
[null,null,null,null,null,null,null,"10:30:00",0.23243,0.23243]
[null,null,null,null,null,null,null,"10:40:00",0.25176999999999999,0.25176999999999999]
[null,null,null,null,null,null,null,"10:50:00",0.27544000000000002,0.27544000000000002]
[null,null,null,null,null,null,null,"11:00:00",0.30518000000000001,0.30518000000000001]
[null,null,null,null,null,null,null,"11:10:00",0.34387000000000001,0.34387000000000001]
[null,null,null,null,null,null,null,"11:20:00",0.39660000000000001,0.39660000000000001]
[null,null,null,null,null,null,null,"11:30:00",0.47350999999999999,0.47350999999999999]
[null,null,null,null,null,null,null,"11:40:00",0.59838000000000002,0.59838000000000002]
[null,null,null,null,null,null,null,"11:50:00",0.84641,0.84641]
[null,null,null,null,null,null,null,"12:00:00",1.80097,1.80097]
[null,null,null,null,null,null,null,"12:10:00",1.1074299999999999,1.1074299999999999]
[null,null,null,null,null,null,null,"12:20:00",0.69716999999999996,0.69716999999999996]
[null,null,null,null,null,null,null,"12:30:00",0.52737999999999996,0.52737999999999996]
[null,null,null,null,null,null,null,"12:40:00",0.43104999999999999,0.43104999999999999]
[null,null,null,null,null,null,null,"12:50:00",0.36802000000000001,0.36802000000000001]
[null,null,null,null,null,null,null,"13:00:00",0.32316,0.32316]
[null,null,null,null,null,null,null,"13:10:00",0.28941,0.28941]
[null,null,null,null,null,null,null,"13:20:00",0.26296999999999998,0.26296999999999998]
[null,null,null,null,null,null,null,"13:30:00",0.24163999999999999,0.24163999999999999]
[null,null,null,null,null,null,null,"13:40:00",0.22402,0.22402]
[null,null,null,null,null,null,null,"13:50:00",0.20918,0.20918]
[null,null,null,null,null,null,null,"14:00:00",0.19649,0.19649]
[null,null,null,null,null,null,null,"14:10:00",0.18551000000000001,0.18551000000000001]
[null,null,null,null,null,null,null,"14:20:00",0.17588999999999999,0.17588999999999999]
[null,null,null,null,null,null,null,"14:30:00",0.16739000000000001,0.16739000000000001]
[null,null,null,null,null,null,null,"14:40:00",0.15981000000000001,0.15981000000000001]
[null,null,null,null,null,null,null,"14:50:00",0.15301000000000001,0.15301000000000001]
[null,null,null,null,null,null,null,"15:00:00",0.14687,0.14687]
[null,null,null,null,null,null,null,"15:10:00",0.14129,0.14129]
[null,null,null,null,null,null,null,"15:20:00",0.13619000000000001,0.13619000000000001]
[null,null,null,null,null,null,null,"15:30:00",0.13152,0.13152]
[null,null,null,null,null,null,null,"15:40:00",0.12722,0.12722]
[null,null,null,null,null,null,null,"15:50:00",0.12324,0.12324]
[null,null,null,null,null,null,null,"16:00:00",0.11955,0.11955]
[null,null,null,null,null,null,null,"16:10:00",0.11612,0.11612]
[null,null,null,null,null,null,null,"16:20:00",0.11292000000000001,0.11292000000000001]
[null,null,null,null,null,null,null,"16:30:00",0.10992,0.10992]
[null,null,null,null,null,null,null,"16:40:00",0.10711,0.10711]
[null,null,null,null,null,null,null,"16:50:00",0.10446999999999999,0.10446999999999999]
[null,null,null,null,null,null,null,"17:00:00",0.10198,0.10198]
[null,null,null,null,null,null,null,"17:10:00",9.9629999999999996E-2,9.9629999999999996E-2]
[null,null,null,null,null,null,null,"17:20:00",9.7409999999999997E-2,9.7409999999999997E-2]
[null,null,null,null,null,null,null,"17:30:00",9.5310000000000006E-2,9.5310000000000006E-2]
[null,null,null,null,null,null,null,"17:40:00",9.3310000000000004E-2,9.3310000000000004E-2]
[null,null,null,null,null,null,null,"17:50:00",9.1410000000000005E-2,9.1410000000000005E-2]
[null,null,null,null,null,null,null,"18:00:00",8.9599999999999999E-2,8.9599999999999999E-2]
[null,null,null,null,null,null,null,"18:10:00",8.788E-2,8.788E-2]
[null,null,null,null,null,null,null,"18:20:00",8.6239999999999997E-2,8.6239999999999997E-2]
[null,null,null,null,null,null,null,"18:30:00",8.4669999999999995E-2,8.4669999999999995E-2]
[null,null,null,null,null,null,null,"18:40:00",8.3169999999999994E-2,8.3169999999999994E-2]
[null,null,null,null,null,null,null,"18:50:00",8.1729999999999997E-2,8.1729999999999997E-2]
[null,null,null,null,null,null,null,"19:00:00",8.0350000000000005E-2,8.0350000000000005E-2]
[null,null,null,null,null,null,null,"19:10:00",7.9020000000000007E-2,7.9020000000000007E-2]
[null,null,null,null,null,null,null,"19:20:00",7.775E-2,7.775E-2]
[null,null,null,null,null,null,null,"19:30:00",7.6530000000000001E-2,7.6530000000000001E-2]
[null,null,null,null,null,null,null,"19:40:00",7.535E-2,7.535E-2]
[null,null,null,null,null,null,null,"19:50:00",7.4219999999999994E-2,7.4219999999999994E-2]
[null,null,null,null,null,null,null,"20:00:00",7.3120000000000004E-2,7.3120000000000004E-2]
[null,null,null,null,null,null,null,"20:10:00",7.2069999999999995E-2,7.2069999999999995E-2]
[null,null,null,null,null,null,null,"20:20:00",7.1050000000000002E-2,7.1050000000000002E-2]
[null,null,null,null,null,null,null,"20:30:00",7.0069999999999993E-2,7.0069999999999993E-2]
[null,null,null,null,null,null,null,"20:40:00",6.9120000000000001E-2,6.9120000000000001E-2]
[null,null,null,null,null,null,null,"20:50:00",6.8199999999999997E-2,6.8199999999999997E-2]
[null,null,null,null,null,null,null,"21:00:00",6.7309999999999995E-2,6.7309999999999995E-2]
[null,null,null,null,null,null,null,"21:10:00",6.6439999999999999E-2,6.6439999999999999E-2]
[null,null,null,null,null,null,null,"21:20:00",6.5610000000000002E-2,6.5610000000000002E-2]
[null,null,null,null,null,null,null,"21:30:00",6.4799999999999996E-2,6.4799999999999996E-2]
[null,null,null,null,null,null,null,"21:40:00",6.4009999999999997E-2,6.4009999999999997E-2]
[null,null,null,null,null,null,null,"21:50:00",6.3250000000000001E-2,6.3250000000000001E-2]
[null,null,null,null,null,null,null,"22:00:00",6.2509999999999996E-2,6.2509999999999996E-2]
[null,null,null,null,null,null,null,"22:10:00",6.1789999999999998E-2,6.1789999999999998E-2]
[null,null,null,null,null,null,null,"22:20:00",6.1089999999999998E-2,6.1089999999999998E-2]
[null,null,null,null,null,null,null,"22:30:00",6.0409999999999998E-2,6.0409999999999998E-2]
[null,null,null,null,null,null,null,"22:40:00",5.9740000000000001E-2,5.9740000000000001E-2]
[null,null,null,null,null,null,null,"22:50:00",5.91E-2,5.91E-2]
[null,null,null,null,null,null,null,"23:00:00",5.8470000000000001E-2,5.8470000000000001E-2]
[null,null,null,null,null,null,null,"23:10:00",5.7860000000000002E-2,5.7860000000000002E-2]
[null,null,null,null,null,null,null,"23:20:00",5.7259999999999998E-2,5.7259999999999998E-2]
[null,null,null,null,null,null,null,"23:30:00",5.6680000000000001E-2,5.6680000000000001E-2]
[null,null,null,null,null,null,null,"23:40:00",5.611E-2,5.611E-2]
[null,null,null,null,null,null,null,"23:50:00",5.5559999999999998E-2,5.5559999999999998E-2]
[null,null,null,null,null,null,null,1,5.5019999999999999E-2,5.5019999999999999E-2]

{"sheet":"03-①調整池容量の概算","index":7,"n_rows":14,"n_cols":12,"rows_kept":14,"cut":false,"hidden":false,"merged":[[13,3,13,5],[8,8,8,11],[2,1,2,5],[4,4,5,4],[4,5,5,5],[8,4,9,4],[8,5,9,5]]}
["※①自然調節方式により調整地容量を概算する場合に入力してください"]
[]
[null,"入　力　条　件"]
[]
[null,null,"行為後ピーク流入量",null,{"$f":"MAX('02流出計算（QT-Sグラフ）'!$J$5:$J$149)","v":1.80097},"m3/s"]
[null,null,"（浸透考慮後）"]
[]
[null,"調整池諸元"]
[null,null,"許容放流量",null,{"$f":"MAX('01流出計算（Q-Tグラフ）'!$I$5:$I$149)","v":0.40022000000000002},"m3/s",null,null,"概　算　結　果"]
[null,null,"（行為前ピーク流入量）"]
[null,null,null,null,null,null,null,null,null,"必要容量",500,"m3/ha"]
[null,null,"調整池高",null,2,"m"]
[]
[null,"浸透施設条件",null,{"$f":"IF('02流出計算（QT-Sグラフ）'!$B$5=1,\"浸透施設なし\",IF('02流出計算（QT-Sグラフ）'!$B$5=2,\"浸透施設あり\",\"浸透施設あり（貯留浸透モデル_道路管理者用）\"))","v":"浸透施設なし"},null,null,{"$f":"'02流出計算（QT-Sグラフ）'!$B$5","v":1},null,null,"オリフィス径（円管、直径）",0.36799999999999999,"m"]

{"sheet":"04-①調節計算（自然調節方式）","index":8,"n_rows":151,"n_cols":26,"rows_kept":151,"cut":false,"hidden":false,"merged":[[3,20,3,25],[24,15,24,16],[3,1,3,8],[5,12,6,12],[5,13,6,13],[8,12,9,12],[8,13,9,13],[3,10,3,13],[13,15,13,16],[10,15,11,18],[28,15,29,18],[31,15,31,18],[1,1,1,13],[15,15,15,16],[17,15,17,16],[20,15,20,16],[22,15,22,16]]}
[]
[null,"入　力　条　件"]
[]
[null,"設 定 調 整 池 諸 元",null,null,null,null,null,null,null,null,"行 為 後 流 入 量",null,null,null,null,null,null,null,null,null,"計　算　結　果　（時　系　列）"]
[]
[null,"水深-容量",null,null,null,null,"放流口形状",null,null,null,"行為後ピーク流入量",null,{"$f":"MAX('02流出計算（QT-Sグラフ）'!$J$5:$J$149)","v":1.80097},"m3/s",null,null,null,null,null,null,"時刻","行為後流入量","浸透考慮後流入量","許容放流量","調節後放流量","調整池水位"]
[null,"No","水深H（m）","容量V（m3）",null,null,"（口径）",null,null,null,"（浸透考慮後）",null,null,null,null,null,null,null,null,null,"00:00:00",0,0,0.40022000000000002,0,0]
[null,1,0,0,null,1,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"00:10:00",5.5280000000000003E-2,5.5280000000000003E-2,0.40022000000000002,4.8633217082188395E-4,8.8854596479748301E-3]
[null,2,2,{"$f":"ROUNDDOWN('03-①調整池容量の概算'!K11*流出係数算出!H8,-2)","v":3700},null,null,"直径",0.37,"m",null,"許容放流量",null,{"$f":"MAX('01流出計算（Q-Tグラフ）'!$I$5:$I$149)","v":0.40022000000000002},"m3/s",null,null,null,null,null,null,"00:20:00",5.5829999999999998E-2,5.5829999999999998E-2,0.40022000000000002,2.5270560876563077E-3,2.641463993038377E-2]
[null,3,null,null,null,null,null,null,null,null,"（行為前ピーク流入量）",null,null,null,null,null,null,null,null,null,"00:30:00",5.6390000000000003E-2,5.6390000000000003E-2,0.40022000000000002,5.3244748989074268E-3,4.333925652715722E-2]
[null,4,null,null,null,null,null,null,null,null,null,null,null,null,null,"計　算　結　果",null,null,null,null,"00:40:00",5.697E-2,5.697E-2,0.40022000000000002,8.5551513330085829E-3,5.9471209030089761E-2]
[null,5,null,null,null,null,"高さ",0.2,"m",null,null,null,null,null,null,null,null,null,null,null,"00:50:00",5.756E-2,5.756E-2,0.40022000000000002,1.2052062845156893E-2,7.4701931055252108E-2]
[null,6,null,null,null,null,"幅",0.2,"m",null,null,null,null,null,null,null,null,null,null,null,"01:00:00",5.8160000000000003E-2,5.8160000000000003E-2,0.40022000000000002,1.5668432351822033E-2,8.8972121023309592E-2]
[null,7,null,null,null,null,null,null,null,null,null,null,null,null,null,"総合評価",null,"O.K",null,null,"01:10:00",5.8779999999999999E-2,5.8779999999999999E-2,0.40022000000000002,1.9276245171891651E-2,0.10226865980324791]
[null,8,null,null,null,null,"（管底位置）",null,null,null,null,null,null,null,null,null,null,null,null,null,"01:20:00",5.9420000000000001E-2,5.9420000000000001E-2,0.40022000000000002,2.2905123766583373E-2,0.1145960053807925]
[null,9,null,null,null,null,"池底高から",0,"m",null,null,null,null,null,null,"放流量評価",null,"許容放流量以下",null,null,"01:30:00",6.0069999999999998E-2,6.0069999999999998E-2,0.40022000000000002,2.6390875648799363E-2,0.12597881628640611]
[null,10,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"01:40:00",6.0740000000000002E-2,6.0740000000000002E-2,0.40022000000000002,2.975753545604902E-2,0.13646447935048472]
[null,11,null,null,null,null,null,null,null,null,null,null,null,null,null,"池の容量不足",null,"無",null,null,"01:50:00",6.1429999999999998E-2,6.1429999999999998E-2,0.40022000000000002,3.2966700304637983E-2,0.14610433301091388]
[null,12,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"02:00:00",6.2140000000000001E-2,6.2140000000000001E-2,0.40022000000000002,3.5985429253160089E-2,0.1549612849745142]
[null,13,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"02:10:00",6.2880000000000005E-2,6.2880000000000005E-2,0.40022000000000002,3.8872631520710625E-2,0.1630956534976703]
[null,14,null,null,null,null,null,null,null,null,null,null,null,null,null,"最大放流量",null,0.38153005284558172,"m3/s",null,"02:20:00",6.3630000000000006E-2,6.3630000000000006E-2,0.40022000000000002,4.1609740902909441E-2,0.17055959310465085]
[null,15,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"02:30:00",6.4399999999999999E-2,6.4399999999999999E-2,0.40022000000000002,4.4134769644774759E-2,0.17741669950232369]
[null,16,null,null,null,null,null,null,null,null,null,null,null,null,null,"池内最大水深",null,1.9694138398645866,"m",null,"02:40:00",6.5199999999999994E-2,6.5199999999999994E-2,0.40022000000000002,4.6477098121877031E-2,0.18373909932394772]
[null,17,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"02:50:00",6.6019999999999995E-2,6.6019999999999995E-2,0.40022000000000002,4.8718222887958018E-2,0.1895809391601907]
[null,18,null,null,null,null,null,null,null,null,null,null,null,null,null,"池内最大ボリューム",null,3643.4156037494854,"m3",null,"03:00:00",6.6869999999999999E-2,6.6869999999999999E-2,0.40022000000000002,5.0803265514946142E-2,0.19499204914890894]
[null,19,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"03:10:00",6.7750000000000005E-2,6.7750000000000005E-2,0.40022000000000002,5.2820521506739875E-2,0.20001846206431123]
[null,20,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"03:20:00",6.8650000000000003E-2,6.8650000000000003E-2,0.40022000000000002,5.4668083402574112E-2,0.20470679640334138]
[null,21,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"03:30:00",6.9589999999999999E-2,6.9589999999999999E-2,0.40022000000000002,5.6437828935368126E-2,0.20910691872691833]
[null,22,null,null,null,null,null,null,null,null,null,null,null,null,null,"許 可 申 請 図 書 の 作 成",null,null,null,null,"03:40:00",7.0559999999999998E-2,7.0559999999999998E-2,0.40022000000000002,5.8126424851850732E-2,0.21325595865331526]
[null,23,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"03:50:00",7.1559999999999999E-2,7.1559999999999999E-2,0.40022000000000002,5.9730778689600673E-2,0.21719046618713395]
[null,24,null,null,null,null,null,null,null,null,null,null,null,null,null,"■【様式】許可申請図書の保存場所",null,null,null,null,"04:00:00",7.2590000000000002E-2,7.2590000000000002E-2,0.40022000000000002,6.1298820319446369E-2,0.22093972040188306]
[null,25,null,null,null,null,null,null,null,null,null,null,null,null,null,"C:\\【様式】許可申請図書.xls",null,null,null,null,"04:10:00",7.3669999999999999E-2,7.3669999999999999E-2,0.40022000000000002,6.282912173546934E-2,0.22452870277135617]
[null,26,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"04:20:00",7.4779999999999999E-2,7.4779999999999999E-2,0.40022000000000002,6.4268706951136512E-2,0.22799121703839306]
[null,27,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"04:30:00",7.5929999999999997E-2,7.5929999999999997E-2,0.40022000000000002,6.5719122186424575E-2,0.23135156907013993]
[null,28,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"04:40:00",7.7130000000000004E-2,7.7130000000000004E-2,0.40022000000000002,6.7075563430346041E-2,0.23463783626742035]
[null,29,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"04:50:00",7.8380000000000005E-2,7.8380000000000005E-2,0.40022000000000002,6.8441210664068663E-2,0.23787998100886662]
[null,30,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"05:00:00",7.9680000000000001E-2,7.9680000000000001E-2,0.40022000000000002,6.9869060633837396E-2,0.24108263971731431]
[null,31,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"05:10:00",8.1030000000000005E-2,8.1030000000000005E-2,0.40022000000000002,7.1253284323999258E-2,0.24425901621063809]
[null,32,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"05:20:00",8.2439999999999999E-2,8.2439999999999999E-2,0.40022000000000002,7.2646530438572207E-2,0.24743255976265352]
[null,33,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"05:30:00",8.3909999999999998E-2,8.3909999999999998E-2,0.40022000000000002,7.4048740923803633E-2,0.25061981305524123]
[null,34,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"05:40:00",8.5440000000000002E-2,8.5440000000000002E-2,0.40022000000000002,7.545985883236099E-2,0.25383733741910641]
[null,35,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"05:50:00",8.7050000000000002E-2,8.7050000000000002E-2,0.40022000000000002,7.6934618520113893E-2,0.25709607082140779]
[null,36,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"06:00:00",8.8730000000000003E-2,8.8730000000000003E-2,0.40022000000000002,7.847401569822994E-2,0.26039953554275747]
[null,37,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"06:10:00",9.0499999999999997E-2,9.0499999999999997E-2,0.40022000000000002,7.996803135497893E-2,0.26377055493953439]
[null,38,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"06:20:00",9.2350000000000002E-2,9.2350000000000002E-2,0.40022000000000002,8.1527269410003489E-2,0.26723347913980755]
[null,39,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"06:30:00",9.4299999999999995E-2,9.4299999999999995E-2,0.40022000000000002,8.3208981804798188E-2,0.27078706002389374]
[null,40,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"06:40:00",9.6350000000000005E-2,9.6350000000000005E-2,0.40022000000000002,8.4902101013005563E-2,0.27444201956695258]
[null,41,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"06:50:00",9.851E-2,9.851E-2,0.40022000000000002,8.6606550696542828E-2,0.27822872469513393]
[null,42,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"07:00:00",0.10079,0.10079,0.40022000000000002,8.8437034781080989E-2,0.28216219732038411]
[null,43,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"07:10:00",0.10321,0.10321,0.40022000000000002,9.0395856693094953E-2,0.28624335005430157]
[null,44,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"07:20:00",0.10577,0.10577,0.40022000000000002,9.236893099303907E-2,0.29049446556465819]
[null,45,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"07:30:00",0.1085,0.1085,0.40022000000000002,9.4532174794577845E-2,0.29493266462612572]
[null,46,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"07:40:00",0.1114,0.1114,0.40022000000000002,9.6771192310480786E-2,0.29956995644692702]
[null,47,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"07:50:00",0.11448999999999999,0.11448999999999999,0.40022000000000002,9.9146851678600031E-2,0.30443027363788688]
[null,48,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"08:00:00",0.11781,0.11781,0.40022000000000002,0.10166187801334256,0.30953696612027454]
[null,49,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"08:10:00",0.12136,0.12136,0.40022000000000002,0.10431909562059988,0.31491897039585148]
[null,50,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"08:20:00",0.12519,0.12519,0.40022000000000002,0.10712142394463424,0.32061239965554322]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"08:30:00",0.12933,0.12933,0.40022000000000002,0.11019538791129636,0.32664534908431125]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"08:40:00",0.13381000000000001,0.13381000000000001,0.40022000000000002,0.11342291468707087,0.33305427298727874]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"08:50:00",0.13868,0.13868,0.40022000000000002,0.11693327163204471,0.3398867833139087]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"09:00:00",0.14401,0.14401,0.40022000000000002,0.12073373677527104,0.34718780897758722]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"09:10:00",0.14985999999999999,0.14985999999999999,0.40022000000000002,0.12483197960770571,0.35502093605061802]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"09:20:00",0.15631999999999999,0.15631999999999999,0.40022000000000002,0.1293663409406188,0.36345039758332215]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"09:30:00",0.16349,0.16349,0.40022000000000002,0.1342180881654996,0.37256805772827589]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"09:40:00",0.17151,0.17151,0.40022000000000002,0.13966344251370447,0.38247916086137795]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"09:50:00",0.18054999999999999,0.18054999999999999,0.40022000000000002,0.14558698711984538,0.39331314524512662]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"10:00:00",0.19081000000000001,0.19081000000000001,0.40022000000000002,0.15227947818876125,0.40523101573562287]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"10:10:00",0.2026,0.2026,0.40022000000000002,0.15977008795712161,0.41842459960385808]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"10:20:00",0.21629999999999999,0.21629999999999999,0.40022000000000002,0.16823241182975049,0.43316473477355449]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"10:30:00",0.23243,0.23243,0.40022000000000002,0.1752746111855199,0.45022792023053765]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"10:40:00",0.25176999999999999,0.25176999999999999,0.40022000000000002,0.17753229971044543,0.47153490765281358]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"10:50:00",0.27544000000000002,0.27544000000000002,0.40022000000000002,0.18042214102235013,0.49898175510154941]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"11:00:00",0.30518000000000001,0.30518000000000001,0.40022000000000002,0.18413765128051332,0.53401854553892292]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"11:10:00",0.34387000000000001,0.34387000000000001,0.40022000000000002,0.18885944556692905,0.57878388118528357]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"11:20:00",0.39660000000000001,0.39660000000000001,0.40022000000000002,0.19497455620015594,0.63661674576359417]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"11:30:00",0.47350999999999999,0.47350999999999999,0.40022000000000002,0.20744066569381764,0.71245914221322004]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"11:40:00",0.59838000000000002,0.59838000000000002,0.40022000000000002,0.22683864581305765,0.81585547007697001]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"11:50:00",0.84641,0.84641,0.40022000000000002,0.25341947911046198,0.97226604441369657]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"12:00:00",1.80097,1.80097,0.40022000000000002,0.30312321604748776,1.311320742496191]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"12:10:00",1.1074299999999999,1.1074299999999999,0.40022000000000002,0.34887919925825367,1.6772230535276926]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"12:20:00",0.69716999999999996,0.69716999999999996,0.40022000000000002,0.36892471849512598,1.8534602560541715]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"12:30:00",0.52737999999999996,0.52737999999999996,0.40022000000000002,0.37739704928870021,1.9310107801973346]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"12:40:00",0.43104999999999999,0.43104999999999999,0.40022000000000002,0.38087701495883164,1.9634684995085456]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"12:50:00",0.36802000000000001,0.36802000000000001,0.40022000000000002,0.38153005284558172,1.9694138398645866]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"13:00:00",0.32316,0.32316,0.40022000000000002,0.3803014140226092,1.9579568452373126]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"13:10:00",0.28941,0.28941,0.40022000000000002,0.37775307859769314,1.9343647653529392]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"13:20:00",0.26296999999999998,0.26296999999999998,0.40022000000000002,0.37424406565489121,1.9019944176363042]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"13:30:00",0.24163999999999999,0.24163999999999999,0.40022000000000002,0.36998932339101842,1.8631365707639944]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"13:40:00",0.22402,0.22402,0.40022000000000002,0.3651400739558216,1.8194388306536959]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"13:50:00",0.20918,0.20918,0.40022000000000002,0.35981067156678481,1.7721278989473275]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"14:00:00",0.19649,0.19649,0.40022000000000002,0.35409193386752186,1.7221442332012238]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"14:10:00",0.18551000000000001,0.18551000000000001,0.40022000000000002,0.34807911355125809,1.6702246038900703]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"14:20:00",0.17588999999999999,0.17588999999999999,0.40022000000000002,0.34177125679189752,1.6169623816722611]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"14:30:00",0.16739000000000001,0.16739000000000001,0.40022000000000002,0.33524082589914428,1.5628436655602005]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"14:40:00",0.15981000000000001,0.15981000000000001,0.40022000000000002,0.32855032415438501,1.5082613169028714]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"14:50:00",0.15301000000000001,0.15301000000000001,0.40022000000000002,0.32168976425485862,1.4535445458094804]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"15:00:00",0.14687,0.14687,0.40022000000000002,0.31467966783817086,1.3989786919565568]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"15:10:00",0.14129,0.14129,0.40022000000000002,0.30757456450618398,1.3448012488736882]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"15:20:00",0.13619000000000001,0.13619000000000001,0.40022000000000002,0.30040086184237924,1.2912073959522998]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"15:30:00",0.13152,0.13152,0.40022000000000002,0.29311955464648193,1.2383732743595113]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"15:40:00",0.12722,0.12722,0.40022000000000002,0.28582694935352065,1.186447895332484]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"15:50:00",0.12324,0.12324,0.40022000000000002,0.27845064611413001,1.135558555526919]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"16:00:00",0.11955,0.11955,0.40022000000000002,0.27107565995511546,1.0858175329210953]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"16:10:00",0.11612,0.11612,0.40022000000000002,0.26366433783297044,1.0373196954419464]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"16:20:00",0.11292000000000001,0.11292000000000001,0.40022000000000002,0.25627181670599813,0.99014734605724875]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"16:30:00",0.10992,0.10992,0.40022000000000002,0.24889977179335299,0.94436384521951611]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"16:40:00",0.10711,0.10711,0.40022000000000002,0.24150885056215671,0.90003217672943348]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"16:50:00",0.10446999999999999,0.10446999999999999,0.40022000000000002,0.23418232212752041,0.85720333791489134]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"17:00:00",0.10198,0.10198,0.40022000000000002,0.22686059342316348,0.81591800025802363]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"17:10:00",9.9629999999999996E-2,9.9629999999999996E-2,0.40022000000000002,0.21958949583640519,0.77621420199971525]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"17:20:00",9.7409999999999997E-2,9.7409999999999997E-2,0.40022000000000002,0.2123976720945312,0.73811466125415803]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"17:30:00",9.5310000000000006E-2,9.5310000000000006E-2,0.40022000000000002,0.20529345371145677,0.70163285706940326]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"17:40:00",9.3310000000000004E-2,9.3310000000000004E-2,0.40022000000000002,0.19823603237170748,0.66678267013699832]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"17:50:00",9.1410000000000005E-2,9.1410000000000005E-2,0.40022000000000002,0.19460042495888258,0.63303405543474045]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"18:00:00",8.9599999999999999E-2,8.9599999999999999E-2,0.40022000000000002,0.191091331937284,0.59984241918130798]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"18:10:00",8.788E-2,8.788E-2,0.40022000000000002,0.1876338432248266,0.56720806645231703]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"18:20:00",8.6239999999999997E-2,8.6239999999999997E-2,0.40022000000000002,0.18425376097608093,0.53513764414946718]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"18:30:00",8.4669999999999995E-2,8.4669999999999995E-2,0.40022000000000002,0.1809252830364764,0.50363455593121464]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"18:40:00",8.3169999999999994E-2,8.3169999999999994E-2,0.40022000000000002,0.17764840940601304,0.47270476796756777]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"18:50:00",8.1729999999999997E-2,8.1729999999999997E-2,0.40022000000000002,0.17366669439172869,0.44247529167604205]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"19:00:00",8.0350000000000005E-2,8.0350000000000005E-2,0.40022000000000002,0.15781658083512731,0.41500449028790326]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"19:10:00",7.9020000000000007E-2,7.9020000000000007E-2,0.40022000000000002,0.1447744097622797,0.39177946478562103]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"19:20:00",7.775E-2,7.775E-2,0.40022000000000002,0.13395431208136824,0.37200237475692138]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"19:30:00",7.6530000000000001E-2,7.6530000000000001E-2,0.40022000000000002,0.12483197960770571,0.35505540853707157]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"19:40:00",7.535E-2,7.535E-2,0.40022000000000002,0.11724842723089721,0.34042831553621705]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"19:50:00",7.4219999999999994E-2,7.4219999999999994E-2,0.40022000000000002,0.11068990676873422,0.32771993704979036]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"20:00:00",7.3120000000000004E-2,7.3120000000000004E-2,0.40022000000000002,0.10516935539073617,0.31660870534825464]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"20:10:00",7.2069999999999995E-2,7.2069999999999995E-2,0.40022000000000002,0.10034186399891545,0.30682688598777058]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"20:20:00",7.1050000000000002E-2,7.1050000000000002E-2,0.40022000000000002,9.606224761468847E-2,0.29818621923961858]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"20:30:00",7.0069999999999993E-2,7.0069999999999993E-2,0.40022000000000002,9.2427177296324284E-2,0.29050469087567055]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"20:40:00",6.9120000000000001E-2,6.9120000000000001E-2,0.40022000000000002,8.9184306583402942E-2,0.28362553132760671]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"20:50:00",6.8199999999999997E-2,6.8199999999999997E-2,0.40022000000000002,8.6264757934814404E-2,0.27744243978411198]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"21:00:00",6.7309999999999995E-2,6.7309999999999995E-2,0.40022000000000002,8.3659368106544188E-2,0.27186177069632411]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"21:10:00",6.6439999999999999E-2,6.6439999999999999E-2,0.40022000000000002,8.1359728530660286E-2,0.26679110637677744]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"21:20:00",6.5610000000000002E-2,6.5610000000000002E-2,0.40022000000000002,7.9247518140615106E-2,0.2621602015111652]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"21:30:00",6.4799999999999996E-2,6.4799999999999996E-2,0.40022000000000002,7.7318514238580355E-2,0.25791868274697133]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"21:40:00",6.4009999999999997E-2,6.4009999999999997E-2,0.40022000000000002,7.5568773701102487E-2,0.25401425767567143]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"21:50:00",6.3250000000000001E-2,6.3250000000000001E-2,0.40022000000000002,7.3994644681923558E-2,0.2503974871270726]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"22:00:00",6.2509999999999996E-2,6.2509999999999996E-2,0.40022000000000002,7.2485312678811809E-2,0.24703749404154796]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"22:10:00",6.1789999999999998E-2,6.1789999999999998E-2,0.40022000000000002,7.109310462905484E-2,0.24391126420783985]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"22:20:00",6.1089999999999998E-2,6.1089999999999998E-2,0.40022000000000002,6.9816002242164651E-2,0.24098762525575018]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"22:30:00",6.0409999999999998E-2,6.0409999999999998E-2,0.40022000000000002,6.8652123393250525E-2,0.23823603731487206]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"22:40:00",5.9740000000000001E-2,5.9740000000000001E-2,0.40022000000000002,6.7494784946006373E-2,0.23564194407066824]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"22:50:00",5.91E-2,5.91E-2,0.40022000000000002,6.6448365907473134E-2,0.2331927844728067]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"23:00:00",5.8470000000000001E-2,5.8470000000000001E-2,0.40022000000000002,6.5511260009194383E-2,0.23085933162145522]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"23:10:00",5.7860000000000002E-2,5.7860000000000002E-2,0.40022000000000002,6.4526917714572765E-2,0.22863638388246596]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"23:20:00",5.7259999999999998E-2,5.7259999999999998E-2,0.40022000000000002,6.3650410989505038E-2,0.22651897922775063]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"23:30:00",5.6680000000000001E-2,5.6680000000000001E-2,0.40022000000000002,6.2777909302537308E-2,0.22449384620741944]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"23:40:00",5.611E-2,5.611E-2,0.40022000000000002,6.1960406363237623E-2,0.22255628150486134]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"23:50:00",5.5559999999999998E-2,5.5559999999999998E-2,0.40022000000000002,6.1197248136312853E-2,0.22069341861304237]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,5.5019999999999999E-2,5.5019999999999999E-2,0.40022000000000002,6.043724913536086E-2,0.21890079743385202]

{"sheet":"04-②調節計算（2段）","index":9,"n_rows":151,"n_cols":26,"rows_kept":151,"cut":false,"hidden":false,"merged":[[14,10,15,11],[14,12,15,12],[14,13,15,13],[15,15,15,16],[8,10,9,11],[8,12,9,12],[8,13,9,13],[11,10,12,11],[11,12,12,12],[11,13,12,13],[13,15,13,16],[10,15,11,18],[1,1,1,13],[3,1,3,8],[3,10,3,13],[5,12,6,12],[5,13,6,13],[28,15,29,18],[31,15,31,18],[3,20,3,25],[26,15,26,16],[17,15,17,16],[20,15,20,16],[22,15,22,16],[24,15,24,16]]}
[]
[null,"入　力　条　件"]
[]
[null,"設 定 調 整 池 諸 元",null,null,null,null,null,null,null,null,"行 為 後 流 入 量",null,null,null,null,null,null,null,null,null,"計　算　結　果　（時　系　列）"]
[]
[null,"水深-容量",null,null,null,null,"■上段オリフィス",null,null,null,"行為後ピーク流入量",null,{"$f":"MAX('02流出計算（QT-Sグラフ）'!$J$5:$J$149)","v":1.80097},"m3/s",null,null,null,null,null,null,"時刻","行為後流入量","浸透考慮後流入量","許容放流量","調節後放流量","調整池水位"]
[null,"No","水深H（m）","容量V（m3）",null,null,"放流口形状",null,null,null,"（浸透考慮後）",null,null,null,null,null,null,null,null,null,"00:00:00",0,0,1.933E-2,0,0]
[null,1,0,0,null,1,"（口径）",null,null,null,null,null,null,null,null,null,null,null,null,null,"00:10:00",2.0999999999999999E-3,0,1.933E-2,0,0]
[null,2,3,300,null,null,null,null,null,null,"許容放流量（計）",null,{"$f":"MAX('01流出計算（Q-Tグラフ）'!$I$5:$I$149)","v":0.40022000000000002},"m3/s",null,null,null,null,null,null,"00:20:00",2.1700000000000001E-3,0,1.933E-2,0,0]
[null,3,null,null,null,null,"直径",0.1,"m",null,null,null,null,null,null,null,null,null,null,null,"00:30:00",2.1700000000000001E-3,0,1.933E-2,0,0]
[null,4,null,null,null,null,null,null,null,null,null,null,null,null,null,"計　算　結　果",null,null,null,null,"00:40:00",2.1700000000000001E-3,0,1.933E-2,0,0]
[null,5,null,null,null,null,null,null,null,null,"許容放流量（上段）",null,null,"m3/s",null,null,null,null,null,null,"00:50:00",2.2499999999999998E-3,0,1.933E-2,0,0]
[null,6,null,null,null,null,"高さ",null,"m",null,null,null,null,null,null,null,null,null,null,null,"01:00:00",2.2499999999999998E-3,0,1.933E-2,0,0]
[null,7,null,null,null,null,"幅",null,"m",null,null,null,null,null,null,"総合評価",null,"O.K",null,null,"01:10:00",2.2499999999999998E-3,0,1.933E-2,0,0]
[null,8,null,null,null,null,null,null,null,null,"許容放流量（下段）",null,{"$f":"M9-M12","v":0.40022000000000002},"m3/s",null,null,null,null,null,null,"01:20:00",2.33E-3,0,1.933E-2,0,0]
[null,9,null,null,null,null,"（管底位置）",null,null,null,null,null,null,null,null,"放流量評価",null,"許容放流量以下",null,null,"01:30:00",2.33E-3,0,1.933E-2,0,0]
[null,10,null,null,null,null,"池底高から",1,"m",null,null,null,null,null,null,null,null,null,null,null,"01:40:00",2.33E-3,0,1.933E-2,0,0]
[null,11,null,null,null,null,null,null,null,null,null,null,null,null,null,"池の容量不足",null,"無",null,null,"01:50:00",2.3999999999999998E-3,0,1.933E-2,0,0]
[null,12,null,null,null,null,"■下段オリフィス",null,null,null,null,null,null,null,null,null,null,null,null,null,"02:00:00",2.3999999999999998E-3,0,1.933E-2,0,0]
[null,13,null,null,null,null,"放流口形状",null,null,null,null,null,null,null,null,null,null,null,null,null,"02:10:00",2.47E-3,0,1.933E-2,0,0]
[null,14,null,null,null,null,"（口径）",null,null,null,null,null,null,null,null,"最大放流量（上段+下段）",null,2.4454520287668694E-3,"m3/s",null,"02:20:00",2.47E-3,0,1.933E-2,0,0]
[null,15,null,null,null,2,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"02:30:00",2.47E-3,0,1.933E-2,0,0]
[null,16,null,null,null,null,"直径",null,"m",null,null,null,null,null,null,"最大放流量（下段）",null,2.4454520287668694E-3,"m3/s",null,"02:40:00",2.5500000000000002E-3,0,1.933E-2,0,0]
[null,17,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"02:50:00",2.5500000000000002E-3,0,1.933E-2,0,0]
[null,18,null,null,null,null,null,null,null,null,null,null,null,null,null,"池内最大水深",null,0.85246185640973493,"m",null,"03:00:00",2.6199999999999999E-3,0,1.933E-2,0,0]
[null,19,null,null,null,null,"高さ",0.01,"m",null,null,null,null,null,null,null,null,null,null,null,"03:10:00",2.6199999999999999E-3,0,1.933E-2,0,0]
[null,20,null,null,null,null,"幅",0.1,"m",null,null,null,null,null,null,"池内最大ボリューム",null,85.246185640973493,"m3",null,"03:20:00",2.7000000000000001E-3,0,1.933E-2,0,0]
[null,21,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"03:30:00",2.7000000000000001E-3,0,1.933E-2,0,0]
[null,22,null,null,null,null,"（管底位置）",null,null,null,null,null,null,null,null,"許 可 申 請 図 書 の 作 成",null,null,null,null,"03:40:00",2.7799999999999999E-3,0,1.933E-2,0,0]
[null,23,null,null,null,null,"池底高から",0,"m",null,null,null,null,null,null,null,null,null,null,null,"03:50:00",2.7799999999999999E-3,0,1.933E-2,0,0]
[null,24,null,null,null,null,null,null,null,null,null,null,null,null,null,"■申請図書様式の保存場所",null,null,null,null,"04:00:00",2.8500000000000001E-3,0,1.933E-2,0,0]
[null,25,null,null,null,null,null,null,null,null,null,null,null,null,null,"C:\\【様式】許可申請図書.xls",null,null,null,null,"04:10:00",2.9199999999999999E-3,0,1.933E-2,0,0]
[null,26,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"04:20:00",2.9199999999999999E-3,0,1.933E-2,0,0]
[null,27,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"04:30:00",3.0000000000000001E-3,0,1.933E-2,0,0]
[null,28,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"04:40:00",3.0000000000000001E-3,0,1.933E-2,0,0]
[null,29,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"04:50:00",3.0799999999999998E-3,0,1.933E-2,0,0]
[null,30,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"05:00:00",3.15E-3,0,1.933E-2,0,0]
[null,31,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"05:10:00",3.2200000000000002E-3,0,1.933E-2,0,0]
[null,32,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"05:20:00",3.2200000000000002E-3,0,1.933E-2,0,0]
[null,33,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"05:30:00",3.3E-3,0,1.933E-2,0,0]
[null,34,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"05:40:00",3.3700000000000002E-3,0,1.933E-2,0,0]
[null,35,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"05:50:00",3.4499999999999999E-3,0,1.933E-2,0,0]
[null,36,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"06:00:00",3.5300000000000002E-3,0,1.933E-2,0,0]
[null,37,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"06:10:00",3.5999999999999999E-3,0,1.933E-2,0,0]
[null,38,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"06:20:00",3.6800000000000001E-3,0,1.933E-2,0,0]
[null,39,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"06:30:00",3.7499999999999999E-3,0,1.933E-2,0,0]
[null,40,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"06:40:00",3.82E-3,0,1.933E-2,0,0]
[null,41,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"06:50:00",3.8999999999999998E-3,0,1.933E-2,0,0]
[null,42,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"07:00:00",4.0499999999999998E-3,0,1.933E-2,0,0]
[null,43,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"07:10:00",4.1200000000000004E-3,0,1.933E-2,0,0]
[null,44,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"07:20:00",4.1999999999999997E-3,0,1.933E-2,0,0]
[null,45,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"07:30:00",4.3499999999999997E-3,0,1.933E-2,0,0]
[null,46,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"07:40:00",4.4999999999999997E-3,0,1.933E-2,0,0]
[null,47,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"07:50:00",4.5799999999999999E-3,0,1.933E-2,0,0]
[null,48,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"08:00:00",4.7200000000000002E-3,0,1.933E-2,0,0]
[null,49,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"08:10:00",4.8799999999999998E-3,0,1.933E-2,0,0]
[null,50,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"08:20:00",5.0299999999999997E-3,0,1.933E-2,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"08:30:00",5.2500000000000003E-3,0,1.933E-2,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"08:40:00",5.4000000000000003E-3,0,1.933E-2,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"08:50:00",5.62E-3,0,1.933E-2,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"09:00:00",5.8500000000000002E-3,0,1.933E-2,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"09:10:00",6.1500000000000001E-3,0,1.933E-2,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"09:20:00",6.3800000000000003E-3,0,1.933E-2,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"09:30:00",6.7499999999999999E-3,0,1.933E-2,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"09:40:00",7.0499999999999998E-3,0,1.933E-2,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"09:50:00",7.4200000000000004E-3,0,1.933E-2,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"10:00:00",7.9500000000000005E-3,0,1.933E-2,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"10:10:00",8.3999999999999995E-3,0,1.933E-2,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"10:20:00",9.0799999999999995E-3,0,1.933E-2,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"10:30:00",9.75E-3,0,1.933E-2,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"10:40:00",1.065E-2,0,1.933E-2,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"10:50:00",1.17E-2,0,1.933E-2,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"11:00:00",1.3050000000000001E-2,0,1.933E-2,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"11:10:00",1.485E-2,0,1.933E-2,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"11:20:00",1.7330000000000002E-2,0,1.933E-2,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"11:30:00",2.0920000000000001E-2,0,1.933E-2,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"11:40:00",2.6919999999999999E-2,0,1.933E-2,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"11:50:00",3.9149999999999997E-2,0,1.933E-2,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"12:00:00",8.6999999999999994E-2,3.0508715650547653E-2,1.933E-2,7.7066217976004244E-4,8.9214160412362825E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"12:10:00",5.2200000000000003E-2,4.5708999999999993E-2,1.933E-2,1.4696308130147857E-3,0.3111464283856813]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"12:20:00",3.1800000000000002E-2,2.5304000000000004E-2,1.933E-2,1.8954245072014869E-3,0.51409026242503242]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"12:30:00",2.3550000000000001E-2,1.7050999999999993E-2,1.933E-2,2.0985721708461683E-3,0.62917327239088949]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"12:40:00",1.8970000000000001E-2,1.2468999999999989E-2,1.933E-2,2.2220706401209437E-3,0.70477134395798813]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"12:50:00",1.5980000000000001E-2,9.4779999999999847E-3,1.933E-2,2.3034356303411217E-3,0.75703582514660184]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"13:00:00",1.388E-2,7.378E-3,1.933E-2,2.3588586521080487E-3,0.79361694229925428]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"13:10:00",1.2370000000000001E-2,5.8679999999999904E-3,1.933E-2,2.3966228436463465E-3,0.81908849781199111]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"13:20:00",1.1180000000000001E-2,4.6779999999999929E-3,1.933E-2,2.421827475340161E-3,0.83627114685503134]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"13:30:00",1.0200000000000001E-2,3.6980000000000029E-3,1.933E-2,2.4372492419093084E-3,0.84682191670328311]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"13:40:00",9.3799999999999994E-3,2.8779999999999956E-3,1.933E-2,2.4446594135865839E-3,0.85190419073679535]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"13:50:00",8.6999999999999994E-3,2.1979999999999934E-3,1.933E-2,2.4454520287668694E-3,0.85246185640973493]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"14:00:00",8.1799999999999998E-3,1.6779999999999972E-3,1.933E-2,2.4409571396918259E-3,0.84943062890435883]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"14:10:00",7.6499999999999997E-3,1.1480000000000008E-3,1.933E-2,2.4319424383478939E-3,0.84328993017023968]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"14:20:00",7.28E-3,7.7799999999998682E-4,1.933E-2,2.4194256323815783E-3,0.83451382595805113]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"14:30:00",6.8999999999999999E-3,3.9799999999999612E-4,1.933E-2,2.4033520048829717E-3,0.82357349304625738]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"14:40:00",6.5199999999999998E-3,1.7999999999981735E-5,1.933E-2,2.3839205989032016E-3,0.81045967523489881]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"14:50:00",6.2199999999999998E-3,0,1.933E-2,2.3629629754690403E-3,0.79627302451178195]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"15:00:00",6.0000000000000001E-3,0,1.933E-2,2.3418178035449298E-3,0.78215868217474016]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"15:10:00",5.7800000000000004E-3,0,1.933E-2,2.3204799560785907E-3,0.76817178889586957]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"15:20:00",5.5500000000000002E-3,0,1.933E-2,2.2995059931428747E-3,0.75431183104820521]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"15:30:00",5.3200000000000001E-3,0,1.933E-2,2.2783389560022669E-3,0.74057829620076976]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"15:40:00",5.1799999999999997E-3,0,1.933E-2,2.2569734124209349E-3,0.72697235909550018]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"15:50:00",4.9500000000000004E-3,0,1.933E-2,2.2359815640312195E-3,0.71349349416614383]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"16:00:00",4.7999999999999996E-3,0,1.933E-2,2.2147907632550754E-3,0.70014117718428481]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"16:10:00",4.6499999999999996E-3,0,1.933E-2,2.1936897427621803E-3,0.6869157356662331]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"16:20:00",4.4999999999999997E-3,0,1.933E-2,2.1723837713442805E-3,0.67381751512391364]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"16:30:00",4.4299999999999999E-3,0,1.933E-2,2.1511670796773314E-3,0.66084686257084879]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"16:40:00",4.2700000000000004E-3,0,1.933E-2,2.1300423356268063E-3,0.64800323432493634]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"16:50:00",4.1999999999999997E-3,0,1.933E-2,2.1090123021511751E-3,0.63528607041160245]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"17:00:00",4.0499999999999998E-3,0,1.933E-2,2.087770444681958E-3,0.62269572217110314]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"17:10:00",3.98E-3,0,1.933E-2,2.0666228395470471E-3,0.61023254231841606]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"17:20:00",3.8999999999999998E-3,0,1.933E-2,2.0452565834602511E-3,0.59789690404939411]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"17:30:00",3.82E-3,0,1.933E-2,2.0243030918843398E-3,0.58568822502336026]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"17:40:00",3.6800000000000001E-3,0,1.933E-2,2.0031304309598764E-3,0.57360592445482761]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"17:50:00",3.5999999999999999E-3,0,1.933E-2,1.9817315759361812E-3,0.5616513384341395]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"18:00:00",3.5300000000000002E-3,0,1.933E-2,1.9607581541491799E-3,0.54982386924388338]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"18:10:00",3.4499999999999999E-3,0,1.933E-2,1.9395579493952995E-3,0.53812292093324987]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"18:20:00",3.3700000000000002E-3,0,1.933E-2,1.9184601979843105E-3,0.52654886649111099]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"18:30:00",3.3700000000000002E-3,0,1.933E-2,1.8971278352914174E-3,0.51510210239128396]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"18:40:00",3.3E-3,0,1.933E-2,1.8758972540660376E-3,0.50378302712321144]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"18:50:00",3.2200000000000002E-3,0,1.933E-2,1.8547719494253195E-3,0.49259101951273737]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"19:00:00",3.15E-3,0,1.933E-2,1.8337555598075225E-3,0.48152543698503886]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"19:10:00",3.0799999999999998E-3,0,1.933E-2,1.8124954956840582E-3,0.47058668381856411]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"19:20:00",3.0799999999999998E-3,0,1.933E-2,1.7913437366436683E-3,0.45977516612158098]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"19:30:00",3.0000000000000001E-3,0,1.933E-2,1.7703041648082683E-3,0.44909022241722518]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"19:40:00",2.9199999999999999E-3,0,1.933E-2,1.7490115177043572E-3,0.43853227536968725]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"19:50:00",2.9199999999999999E-3,0,1.933E-2,1.7278303546283123E-3,0.42810174975268933]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"20:00:00",2.8500000000000001E-3,0,1.933E-2,1.7067648261769985E-3,0.41779796421027338]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"20:10:00",2.8500000000000001E-3,0,1.933E-2,1.6854360294520226E-3,0.4076213616433863]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"20:20:00",2.7799999999999999E-3,0,1.933E-2,1.6642220522101309E-3,0.39757238739839984]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"20:30:00",2.7799999999999999E-3,0,1.933E-2,1.6431273416681678E-3,0.38765033921676501]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"20:40:00",2.7000000000000001E-3,0,1.933E-2,1.6221565507064969E-3,0.37785448753964102]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"20:50:00",2.7000000000000001E-3,0,1.933E-2,1.6009110809356338E-3,0.36818528464471456]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"21:00:00",2.6199999999999999E-3,0,1.933E-2,1.579788813516699E-3,0.35864318496135761]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"21:10:00",2.6199999999999999E-3,0,1.933E-2,1.5583802814340599E-3,0.34922867767650528]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"21:20:00",2.5500000000000002E-3,0,1.933E-2,1.5370938487938852E-3,0.3399422552858215]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"21:30:00",2.5500000000000002E-3,0,1.933E-2,1.5159346590882469E-3,0.33078316976217509]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"21:40:00",2.47E-3,0,1.933E-2,1.4949081153828483E-3,0.32175064143876181]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"21:50:00",2.47E-3,0,1.933E-2,1.4740198941796882E-3,0.31284385741007414]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"22:00:00",2.3999999999999998E-3,0,1.933E-2,1.4528313816260646E-3,0.30406330358265693]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"22:10:00",2.3999999999999998E-3,0,1.933E-2,1.4313292418020043E-3,0.29541082171237271]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"22:20:00",2.3999999999999998E-3,0,1.933E-2,1.4104154557478799E-3,0.28688558761972305]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"22:30:00",2.33E-3,0,1.933E-2,1.3891868546698461E-3,0.27848678068846988]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"22:40:00",2.33E-3,0,1.933E-2,1.3681010447879937E-3,0.27021491699009642]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"22:50:00",2.33E-3,0,1.933E-2,1.346685122926848E-3,0.26207055848695188]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"23:00:00",2.2499999999999998E-3,0,1.933E-2,1.3258978679558996E-3,0.25405280951430359]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"23:10:00",2.2499999999999998E-3,0,1.933E-2,1.3042842864958543E-3,0.24616226305094832]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"23:20:00",2.2499999999999998E-3,0,1.933E-2,1.2833136125378706E-3,0.23839946935384718]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"23:30:00",2.1700000000000001E-3,0,1.933E-2,1.2619945151425976E-3,0.23076354497080578]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"23:40:00",2.1700000000000001E-3,0,1.933E-2,1.2408297532548532E-3,0.22325507216561344]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"23:50:00",2.1700000000000001E-3,0,1.933E-2,1.2198273603516603E-3,0.21587310082479386]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,2.0999999999999999E-3,0,1.933E-2,1.1984569669214243E-3,0.20861824784297461]

{"sheet":"04-③調節計算（ポンプ）","index":10,"n_rows":151,"n_cols":26,"rows_kept":151,"cut":false,"hidden":false,"merged":[[11,9,12,10],[11,11,12,11],[11,12,12,12],[14,9,15,10],[1,1,1,12],[3,9,3,12],[5,11,6,11],[5,12,6,12],[8,11,9,11],[8,12,9,12],[3,1,3,3],[3,5,3,7],[31,15,31,18],[22,15,22,16],[28,15,29,18],[14,11,15,11],[3,20,3,25],[13,15,13,16],[15,15,15,16],[17,15,17,16],[14,12,15,12],[24,15,24,16],[10,15,11,18],[20,15,20,16]]}
[]
[null,"入　力　条　件"]
[]
[null,"設 定 調 整 池 諸 元",null,null,null,"放 流 ポ ン プ 諸 元",null,null,null,"行 為 後 流 入 量",null,null,null,null,null,null,null,null,null,null,"計　算　結　果　（時　系　列）"]
[]
[null,"水深-容量",null,null,null,"水深-ポンプ",null,null,null,"行為後ピーク流入量",null,{"$f":"MAX('02流出計算（QT-Sグラフ）'!$J$5:$J$149)","v":1.80097},"m3/s",null,null,null,null,null,null,null,"時刻","行為後流入量","浸透考慮後流入量","許容放流量","調節後放流量","調整池水位"]
[null,"No","水深H（m）","容量V（m3）",null,"No","水深H（m）","ポンプ規模Q(m3/s)",null,"（浸透考慮後）",null,null,null,null,null,null,null,null,null,null,"00:00:00",0,0,1.933E-2,0,0]
[null,1,0,0,null,1,0,0,null,null,null,null,null,null,null,null,null,null,null,null,"00:10:00",2.0999999999999999E-3,0,1.933E-2,0,0]
[null,2,3,90,null,2,3,1.4999999999999999E-2,null,"許容放流量",null,{"$f":"MAX('01流出計算（Q-Tグラフ）'!$I$5:$I$149)","v":0.40022000000000002},"m3/s",null,null,null,null,null,null,null,"00:20:00",2.1700000000000001E-3,0,1.933E-2,0,0]
[null,3,null,null,null,3,null,null,null,"（行為前ピーク流入量）",null,null,null,null,null,null,null,null,null,null,"00:30:00",2.1700000000000001E-3,0,1.933E-2,0,0]
[null,4,null,null,null,4,null,null,null,null,null,null,null,null,null,"計　算　結　果",null,null,null,null,"00:40:00",2.1700000000000001E-3,0,1.933E-2,0,0]
[null,5,null,null,null,5,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"00:50:00",2.2499999999999998E-3,0,1.933E-2,0,0]
[null,6,null,null,null,6,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"01:00:00",2.2499999999999998E-3,0,1.933E-2,0,0]
[null,7,null,null,null,7,null,null,null,null,null,null,null,null,null,"総合評価",null,"O.K",null,null,"01:10:00",2.2499999999999998E-3,0,1.933E-2,0,0]
[null,8,null,null,null,8,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"01:20:00",2.33E-3,0,1.933E-2,0,0]
[null,9,null,null,null,9,null,null,null,null,null,null,null,null,null,"放流量評価",null,"許容放流量以下",null,null,"01:30:00",2.33E-3,0,1.933E-2,0,0]
[null,10,null,null,null,10,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"01:40:00",2.33E-3,0,1.933E-2,0,0]
[null,11,null,null,null,11,null,null,null,null,null,null,null,null,null,"池の容量不足",null,"無",null,null,"01:50:00",2.3999999999999998E-3,0,1.933E-2,0,0]
[null,12,null,null,null,12,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"02:00:00",2.3999999999999998E-3,0,1.933E-2,0,0]
[null,13,null,null,null,13,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"02:10:00",2.47E-3,0,1.933E-2,0,0]
[null,14,null,null,null,14,null,null,null,null,null,null,null,null,null,"最大放流量",null,9.7851562499999996E-3,"m3/s",null,"02:20:00",2.47E-3,0,1.933E-2,0,0]
[null,15,null,null,null,15,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"02:30:00",2.47E-3,0,1.933E-2,0,0]
[null,16,null,null,null,16,null,null,null,null,null,null,null,null,null,"池内最大水深",null,1.9570632876203276,"m",null,"02:40:00",2.5500000000000002E-3,0,1.933E-2,0,0]
[null,17,null,null,null,17,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"02:50:00",2.5500000000000002E-3,0,1.933E-2,0,0]
[null,18,null,null,null,18,null,null,null,null,null,null,null,null,null,"池内最大ボリューム",null,58.711898628609823,"m3",null,"03:00:00",2.6199999999999999E-3,0,1.933E-2,0,0]
[null,19,null,null,null,19,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"03:10:00",2.6199999999999999E-3,0,1.933E-2,0,0]
[null,20,null,null,null,20,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"03:20:00",2.7000000000000001E-3,0,1.933E-2,0,0]
[null,21,null,null,null,21,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"03:30:00",2.7000000000000001E-3,0,1.933E-2,0,0]
[null,22,null,null,null,22,null,null,null,null,null,null,null,null,null,"許 可 申 請 図 書 の 作 成",null,null,null,null,"03:40:00",2.7799999999999999E-3,0,1.933E-2,0,0]
[null,23,null,null,null,23,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"03:50:00",2.7799999999999999E-3,0,1.933E-2,0,0]
[null,24,null,null,null,24,null,null,null,null,null,null,null,null,null,"■申請図書様式の保存場所",null,null,null,null,"04:00:00",2.8500000000000001E-3,0,1.933E-2,0,0]
[null,25,null,null,null,25,null,null,null,null,null,null,null,null,null,"C:\\【様式】許可申請図書.xls",null,null,null,null,"04:10:00",2.9199999999999999E-3,0,1.933E-2,0,0]
[null,26,null,null,null,26,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"04:20:00",2.9199999999999999E-3,0,1.933E-2,0,0]
[null,27,null,null,null,27,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"04:30:00",3.0000000000000001E-3,0,1.933E-2,0,0]
[null,28,null,null,null,28,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"04:40:00",3.0000000000000001E-3,0,1.933E-2,0,0]
[null,29,null,null,null,29,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"04:50:00",3.0799999999999998E-3,0,1.933E-2,0,0]
[null,30,null,null,null,30,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"05:00:00",3.15E-3,0,1.933E-2,0,0]
[null,31,null,null,null,31,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"05:10:00",3.2200000000000002E-3,0,1.933E-2,0,0]
[null,32,null,null,null,32,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"05:20:00",3.2200000000000002E-3,0,1.933E-2,0,0]
[null,33,null,null,null,33,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"05:30:00",3.3E-3,0,1.933E-2,0,0]
[null,34,null,null,null,34,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"05:40:00",3.3700000000000002E-3,0,1.933E-2,0,0]
[null,35,null,null,null,35,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"05:50:00",3.4499999999999999E-3,0,1.933E-2,0,0]
[null,36,null,null,null,36,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"06:00:00",3.5300000000000002E-3,0,1.933E-2,0,0]
[null,37,null,null,null,37,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"06:10:00",3.5999999999999999E-3,0,1.933E-2,0,0]
[null,38,null,null,null,38,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"06:20:00",3.6800000000000001E-3,0,1.933E-2,0,0]
[null,39,null,null,null,39,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"06:30:00",3.7499999999999999E-3,0,1.933E-2,0,0]
[null,40,null,null,null,40,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"06:40:00",3.82E-3,0,1.933E-2,0,0]
[null,41,null,null,null,41,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"06:50:00",3.8999999999999998E-3,0,1.933E-2,0,0]
[null,42,null,null,null,42,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"07:00:00",4.0499999999999998E-3,0,1.933E-2,0,0]
[null,43,null,null,null,43,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"07:10:00",4.1200000000000004E-3,0,1.933E-2,0,0]
[null,44,null,null,null,44,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"07:20:00",4.1999999999999997E-3,0,1.933E-2,0,0]
[null,45,null,null,null,45,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"07:30:00",4.3499999999999997E-3,0,1.933E-2,0,0]
[null,46,null,null,null,46,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"07:40:00",4.4999999999999997E-3,0,1.933E-2,0,0]
[null,47,null,null,null,47,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"07:50:00",4.5799999999999999E-3,0,1.933E-2,0,0]
[null,48,null,null,null,48,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"08:00:00",4.7200000000000002E-3,0,1.933E-2,0,0]
[null,49,null,null,null,49,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"08:10:00",4.8799999999999998E-3,0,1.933E-2,0,0]
[null,50,null,null,null,50,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"08:20:00",5.0299999999999997E-3,0,1.933E-2,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"08:30:00",5.2500000000000003E-3,0,1.933E-2,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"08:40:00",5.4000000000000003E-3,0,1.933E-2,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"08:50:00",5.62E-3,0,1.933E-2,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"09:00:00",5.8500000000000002E-3,0,1.933E-2,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"09:10:00",6.1500000000000001E-3,0,1.933E-2,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"09:20:00",6.3800000000000003E-3,0,1.933E-2,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"09:30:00",6.7499999999999999E-3,0,1.933E-2,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"09:40:00",7.0499999999999998E-3,0,1.933E-2,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"09:50:00",7.4200000000000004E-3,0,1.933E-2,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"10:00:00",7.9500000000000005E-3,0,1.933E-2,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"10:10:00",8.3999999999999995E-3,0,1.933E-2,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"10:20:00",9.0799999999999995E-3,0,1.933E-2,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"10:30:00",9.75E-3,0,1.933E-2,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"10:40:00",1.065E-2,0,1.933E-2,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"10:50:00",1.17E-2,0,1.933E-2,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"11:00:00",1.3050000000000001E-2,0,1.933E-2,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"11:10:00",1.485E-2,0,1.933E-2,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"11:20:00",1.7330000000000002E-2,0,1.933E-2,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"11:30:00",2.0920000000000001E-2,0,1.933E-2,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"11:40:00",2.6919999999999999E-2,0,1.933E-2,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"11:50:00",3.9149999999999997E-2,0,1.933E-2,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"12:00:00",8.6999999999999994E-2,3.0508715650547653E-2,1.933E-2,1.4529418945312498E-3,0.29055773756016401]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"12:10:00",5.2200000000000003E-2,4.5708999999999993E-2,1.933E-2,4.94384765625E-3,0.98876699855782801]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"12:20:00",3.1800000000000002E-2,2.5304000000000004E-2,1.933E-2,7.8543090820312501E-3,1.5709154311750155]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"12:30:00",2.3550000000000001E-2,1.7050999999999993E-2,1.933E-2,9.1232299804687497E-3,1.8246900405500153]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"12:40:00",1.8970000000000001E-2,1.2468999999999989E-2,1.933E-2,9.6606445312500001E-3,1.9320512954328277]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"12:50:00",1.5980000000000001E-2,9.4779999999999847E-3,1.933E-2,9.7851562499999996E-3,1.9570632876203276]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"13:00:00",1.388E-2,7.378E-3,1.933E-2,9.6560668945312508E-3,1.9312110561750147]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"13:10:00",1.2370000000000001E-2,5.8679999999999904E-3,1.933E-2,9.3667602539062502E-3,1.8734427846906399]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"13:20:00",1.1180000000000001E-2,4.6779999999999929E-3,1.933E-2,8.9776611328125002E-3,1.7954585708234521]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"13:30:00",1.0200000000000001E-2,3.6980000000000029E-3,1.933E-2,8.5208129882812494E-3,1.7042338296125144]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"13:40:00",9.3799999999999994E-3,2.8779999999999956E-3,1.933E-2,8.0227661132812496E-3,1.6045580385968896]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"13:50:00",8.6999999999999994E-3,2.1979999999999934E-3,1.933E-2,7.4999999999999997E-3,1.5000903774640768]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"14:00:00",8.1799999999999998E-3,1.6779999999999972E-3,1.933E-2,6.9708251953124996E-3,1.3941421255109518]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"14:10:00",7.6499999999999997E-3,1.1480000000000008E-3,1.933E-2,6.4416503906250004E-3,1.2882773696515768]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"14:20:00",7.28E-3,7.7799999999998682E-4,1.933E-2,5.9197998046874997E-3,1.1839228676984517]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"14:30:00",6.8999999999999999E-3,3.9799999999999612E-4,1.933E-2,5.4116821289062504E-3,1.082368048362514]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"14:40:00",6.5199999999999998E-3,1.7999999999981735E-5,1.933E-2,4.9163818359374998E-3,0.98324740871407623]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"14:50:00",6.2199999999999998E-3,0,1.933E-2,4.4485473632812503E-3,0.88977811672188856]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"15:00:00",6.0000000000000001E-3,0,1.933E-2,4.0255737304687499E-3,0.80503690578438858]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"15:10:00",5.7800000000000004E-3,0,1.933E-2,3.6419677734374997E-3,0.72836149074532608]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"15:20:00",5.5500000000000002E-3,0,1.933E-2,3.2949829101562495E-3,0.65899198390938851]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"15:30:00",5.3200000000000001E-3,0,1.933E-2,2.9809570312499998E-3,0.59623258449532601]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"15:40:00",5.1799999999999997E-3,0,1.933E-2,2.6971435546874999E-3,0.53945157863595106]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"15:50:00",4.9500000000000004E-3,0,1.933E-2,2.4407958984375001E-3,0.48807218410470105]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"16:00:00",4.7999999999999996E-3,0,1.933E-2,2.208251953125E-3,0.44158170558907606]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"16:10:00",4.6499999999999996E-3,0,1.933E-2,1.9976806640624998E-3,0.39952237941720103]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"16:20:00",4.4999999999999997E-3,0,1.933E-2,1.8072509765625E-3,0.36147306301095106]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"16:30:00",4.4299999999999999E-3,0,1.933E-2,1.6351318359374997E-3,0.32704923488595106]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"16:40:00",4.2700000000000004E-3,0,1.933E-2,1.4794921874999999E-3,0.29590299465157605]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"16:50:00",4.1999999999999997E-3,0,1.933E-2,1.3385009765624998E-3,0.26772306301095106]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"17:00:00",4.0499999999999998E-3,0,1.933E-2,1.2112426757812499E-3,0.24222562648751353]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"17:10:00",3.98E-3,0,1.933E-2,1.0958862304687499E-3,0.21915433742501353]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"17:20:00",3.8999999999999998E-3,0,1.933E-2,9.9151611328125006E-4,0.19828031398751353]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"17:30:00",3.82E-3,0,1.933E-2,8.9721679687500007E-4,0.17939298488595104]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"17:40:00",3.6800000000000001E-3,0,1.933E-2,8.1115722656249995E-4,0.16230924465157603]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"17:50:00",3.5999999999999999E-3,0,1.933E-2,7.3425292968749996E-4,0.14685514308907605]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"18:00:00",3.5300000000000002E-3,0,1.933E-2,6.6467285156250003E-4,0.13286588527657603]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"18:10:00",3.4499999999999999E-3,0,1.933E-2,6.0058593749999999E-4,0.12021329738595105]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"18:20:00",3.3700000000000002E-3,0,1.933E-2,5.4382324218750001E-4,0.10876920558907605]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"18:30:00",3.3700000000000002E-3,0,1.933E-2,4.9163818359374998E-4,9.841459133126354E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"18:40:00",3.3E-3,0,1.933E-2,4.4494628906249995E-4,8.9048746604701037E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"18:50:00",3.2200000000000002E-3,0,1.933E-2,4.0283203125000003E-4,8.0570963401576046E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"19:00:00",3.15E-3,0,1.933E-2,3.6437988281249998E-4,7.2898844260951043E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"19:10:00",3.0799999999999998E-3,0,1.933E-2,3.2958984374999997E-4,6.595914699532604E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"19:20:00",3.0799999999999998E-3,0,1.933E-2,2.9846191406249998E-4,5.9678629417201041E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"19:30:00",3.0000000000000001E-3,0,1.933E-2,2.7008056640624999E-4,5.3993204612513543E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"19:40:00",2.9199999999999999E-3,0,1.933E-2,2.4444580078124999E-4,4.8847940940638539E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"19:50:00",2.9199999999999999E-3,0,1.933E-2,2.2064208984374999E-4,4.4197062034388543E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"20:00:00",2.8500000000000001E-3,0,1.933E-2,1.995849609375E-4,3.9994791526576041E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"20:10:00",2.8500000000000001E-3,0,1.933E-2,1.8127441406250001E-4,3.6186197776576043E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"20:20:00",2.7799999999999999E-3,0,1.933E-2,1.6387939453125E-4,3.2734659690638539E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"20:30:00",2.7799999999999999E-3,0,1.933E-2,1.4831542968750001E-4,2.9612711448451044E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"20:40:00",2.7000000000000001E-3,0,1.933E-2,1.336669921875E-4,2.6792887229701041E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"20:50:00",2.7000000000000001E-3,0,1.933E-2,1.2084960937499999E-4,2.4247721214076041E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"21:00:00",2.6199999999999999E-3,0,1.933E-2,1.0986328124999999E-4,2.1940592307826041E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"21:10:00",2.6199999999999999E-3,0,1.933E-2,9.8876953124999993E-5,1.9853189964076041E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"21:20:00",2.5500000000000002E-3,0,1.933E-2,8.9721679687499998E-5,1.7967203635951043E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"21:30:00",2.5500000000000002E-3,0,1.933E-2,8.1481933593749998E-5,1.6255167503138542E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"21:40:00",2.47E-3,0,1.933E-2,7.3242187499999997E-5,1.4707926292201043E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"21:50:00",2.47E-3,0,1.933E-2,6.6833496093749998E-5,1.3307169456263541E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"22:00:00",2.3999999999999998E-3,0,1.933E-2,6.0424804687499993E-5,1.2034586448451042E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"22:10:00",2.3999999999999998E-3,0,1.933E-2,5.4016113281249994E-5,1.0890177268763542E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"22:20:00",2.3999999999999998E-3,0,1.933E-2,4.9438476562499996E-5,9.8556313703260425E-3]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"22:30:00",2.33E-3,0,1.933E-2,4.4860839843749999E-5,8.9126382062635415E-3]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"22:40:00",2.33E-3,0,1.933E-2,4.0283203125000002E-5,8.0611977765760422E-3]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"22:50:00",2.33E-3,0,1.933E-2,3.6621093749999999E-5,7.2921548078260416E-3]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"23:00:00",2.2499999999999998E-3,0,1.933E-2,3.2958984374999995E-5,6.5963540265760422E-3]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"23:10:00",2.2499999999999998E-3,0,1.933E-2,3.0212402343749996E-5,5.9646401593885416E-3]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"23:20:00",2.2499999999999998E-3,0,1.933E-2,2.655029296875E-5,5.3970132062635418E-3]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"23:30:00",2.1700000000000001E-3,0,1.933E-2,2.4719238281249998E-5,4.8843178937635423E-3]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"23:40:00",2.1700000000000001E-3,0,1.933E-2,2.1972656250000003E-5,4.417398948451042E-3]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"23:50:00",2.1700000000000001E-3,0,1.933E-2,2.0141601562500001E-5,3.9962563703260416E-3]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,2.0999999999999999E-3,0,1.933E-2,1.8310546874999999E-5,3.6117348859510418E-3]